## Shell Distortion Criteria
© POWERS Engineering and Inspection, Inc. 2016
Shell Distortion Assessment
Given:
|  |  |  | Variable Identifier |  | Description | Value | Reference
|  |  |  | H |  | Fill height (ft) | 64 | Measured from the base of each shell course (see column H in the table below)
|  |  |  | D |  | Tank Diameter (ft) | 150
|  |  |  | G |  | Specific Gravity | 0.79
|  |  |  | S |  | Allow stress (psi) | Varies | Reference API 653 Table 4-1
|  |  |  | E |  | Joint Efficiency | Varies | Reference API 653 table 4.2 for Welded and 4.3 for Riveted construction
|  |  |  | M | 1 | Temp Modifier | Varies | Reference API 650 Appendix M Elevated temperature modifier
|  | Table for Calculating minimum shell thickness (t min) for each shell course | [10 empty] | Shell Plumbness Criteira |  |  |  | Roundness Criteria (1-ft above shell) (in)
|  |  | height from laser (ft) |  | H |  | E |  | S |  | Actual | Solution | Allowable Plumbness (in) | Does the tank have an IFR? | New Tank? | Full Shell Height Plumbness Criteria (in)
|  | Course |  |  | Product Height Above Course | Type of Joint for each Course | Joint Eff API 653 Tbl 4.2 and 4.3 | Material Type or Unknown Welded or Riveted | Maximum Allowable Stress | Req'd t min | Minimum Thickness for Course | Actual Vs Req'd
|  |  | (in) | (ft) | (ft) |  | % |  | (psi) | (in) | (in) | OK?
|  | 1 | 120 | 10 | 61.9 | Butt Weld 100% | 1 | A 573 70 | 30030 | 0.6248 | 0.815 | Ok | 2.185 | No | No | 5 | 3
|  | 2 | 240 | 20 | 51.9 | Butt Weld 100% | 1 | A 573 70 | 30030 | 0.5222 | 0.675 | Ok | 2.325
|  | 3 | 360 | 30 | 41.9 | Butt Weld 100% | 1 | A 573 70 | 33040 | 0.3814 | 0.54 | Ok | 2.46
|  | 4 | 480 | 40 | 31.9 | Butt Weld 100% | 1 | A 573 70 | 33040 | 0.2881 | 0.45 | Ok | 2.55
|  | 5 | 576 | 48 | 21.9 | Butt Weld 100% | 1 | A 36 | 27376 | 0.2352 | 0.41 | Ok | 2.59
|  | 6 | 672 | 56 | 13.9 | Butt Weld 100% | 1 | A 36 | 27376 | 0.1452 | 0.36 | Ok | 2.64
|  | 7 | 768 | 64 | 5.9 | Butt Weld 100% | 1 | A 36 | 27376 | 0.1 | 0.312 | Ok | 2.688
| Sum |  | 2448 | 160
Allowances:
|  | Course | Total | Type | Height (ft) | Arc Length (ft) | Arc Length (Degrees) | Arc Length (Degrees) | Arc Length (in) | Type | Height (ft) | Arc Length (ft) | Arc Length (Degrees) | Arc Length (Degrees) | Arc Length (in)
|  |  | (in) | (ft) | % |  |  |  | (ft) | (ft) | % |  |  |  | (ft)
|  | 1 | 3.0752 | Inward | #N/A |  |  |  | Inward | Inward |  |  |  |  | Inward
|  | 2 | 3.0374 | Inward |  |  |  |  | Inward | Inward |  |  |  |  | Inward
|  | 3 | 2.7717 | Inward | 0 |  |  |  | Inward | Inward | 0 |  |  |  | Inward
|  | 4 | 2.7596 | Inward |  |  |  |  | Inward | Inward |  |  |  |  | Inward
|  | 5 | 2.7225 | Inward |  |  |  |  | Inward | Inward |  |  |  |  | Inward
|  | 7 | 2.5039 | Inward |  |  |  |  | Inward | Inward |  |  |  |  | Inward
|  | 8 | 2.4841 | Inward |  |  |  |  | Inward | Inward |  |  |  |  | Inward
|  | 9 | 2.2673 | Inward |  |  |  |  | Inward | Inward |  |  |  |  | Inward
|  | 10 | 2.1548 | Inward |  |  |  |  | Inward | Inward |  |  |  |  | Inward
API 650 or API 653 Individual Shell Course Plumbness Requirement
|  | Shell Course Thickness Range (in) |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft)
[5 empty] | 4 | 5 | 6 | 7 | 8 | 10
|  |  | 0 | 0.25 | 0.9375 | 1.25 | 1.375 | 1.5 | 1.625 | 1.875
|  |  | 0.25 | 0.375 | 0.75 | 0.938 | 1.125 | 1.225 | 1.375 | 1.625
|  |  | 0.375 | 0.5 | 0.625 | 0.625 | 0.75 | 0.875 | 1 | 1.25
|  |  | 0.5 | 0.75 | 0.563 | 0.625 | 0.625 | 0.75 | 1 | 1.125
|  |  | 0.75 | 1 | 0.563 | 0.625 | 0.625 | 0.625 | 0.75 | 1
|  |  | 1 | 2 | 0.5 | 0.563 | 0.563 | 0.625 | 0.625 | 0.688
|  |  | 2 | 4 | 0.438 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625
|  | API 650 7.5.2.b Full Height of Shell Plumbness Requirement (in) |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 3.84; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: in |  | API 653 10.5.2.1 Full Height of Shell Plumbness Requirement, 1/100 of shell or 5-in max (in) |  |  |  | 5 | in | [10 empty] | no | no | api 653
[5 empty] | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.32; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: ft | [5 empty] | 0.41667 | ft | [10 empty] | yes | no | min max
[28 empty] | yes | yes | api 650
|  | API 650 Roundness Requirement Section 1-ft above shell 7.5.3 | [9 empty] | API 653 Roundness Requirement Section 1-ft above shell 10.5.3 | [15 empty] | no | yes | api 650
|  | Tank Diameter (ft) |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: Radii Tolerance |  | Tank Diameter (ft) |  |  | Radii Tolerance | 3x Tolerance
|  | 0 |  | 40 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 0.5 |  | <40 |  |  | 0.5 | 1.5
|  | 40 |  | 150 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 0.75 |  | 40 to 150 |  |  | 0.75 | 2.25
|  | 150 |  | 250 | [7 empty] | 150 to 250 |  |  | 1 | 3 | bar: ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4
|  | 250 |  | 1000 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 1.25 |  | 250 Greater |  |  | 1.25 | 3.75
|  | API 650 H.4.4.3 Radii Requirements | [9 empty] | API 650 H.4.4.3 Radii Requirements
|  | Elevation +/- (in): |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 4 |  | Elevation +/- (in): |  |  | 4
|  | API 650 Peaking Banding (Local Deviations) 7.5.4 | [9 empty] | API 653 Peaking Banding (Local Deviations) 10.5.4
|  | Location Size: |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: Radii Tolerance |  | Location Size: |  |  |  | Radii Tolerance
|  | Peaking (vertical joint), in: |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.5 |  | Peaking (vertical joint), in: |  |  |  | 0.5
|  | Banding (horizontal joint), in: |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.5 |  | Banding (horizontal joint), in: |  |  |  | 1
`
| Shell Corrosion Rate Calculations API 653 6.3 |  |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 8: © POWERS Engineering and Inspection, Inc. 2016
|  | Course | Date(s) |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 7: A; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 8: B; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 10: RCA/4N Next External API 653 6.3.2 | RCA/2N Next UT Inspection API 653 6.3.3
|  |  | Year Built or Replaced | Inspection Year | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: Thickness
[7 empty] | Measured |  | Calculated
|  |  |  | Prev | Current | As Built | Prev | Current | t min
|  |  | (yr) | (yr) | (yr) | (in) | (in) | (in) | (in) | (yr) | (yr)
|  | 1 | 1978 | 2016 | #REF! | 0.625 | 0.625 | 0.625 | #REF! | #REF! | #REF!
|  | 2 | 1978 | 2016 | #REF! | 0.5 | 0.5 | 0.5 | #REF! | #REF! | #REF!
|  | 3 | 1978 | 2016 | #REF! | 0.375 | 0.375 | 0.375 | #REF! | #REF! | #REF!
|  | 4 | 1978 | 2016 | #REF! | 0.3125 | 0.3125 | 0.3125 | #REF! | #REF! | #REF!
|  | 5 | 1978 | 2016 | #REF! | 0.3125 | 0.3125 | 0.3125 | #REF! | #REF! | #REF!
|  | 6 | 1978 | 2016 | #REF! | 0 | 0 | 0 | #REF! | #REF! | #REF!
|  | 7 | 1978 | 2016 | #REF! | 0 | 0 | 0 | #REF! | #REF! | #REF!
|  | 8 | 1978 | 2016 | #REF! | 0.35 | 0 | 0 | #REF! | #REF! | #REF!
|  | 9 | 1978 | 2016 | #REF! | 0 | 0 | 0 | #REF! | #REF! | #REF!
|  | 10 | 1978 | 2016 | #REF! | 0 | 0 | 0 |  | #REF! | #REF!
[5 empty] | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 10: #REF! | #REF!
RCA = The difference between the measured thickness and the minimum required thickness (in per year are used in this calculation) ref API 653 6.3.2.1
*Note: Next External API 653 and UT Inspection calculation(s) not applicable because the tank is coated inside and out reducing the corrosion rate to 0.
SHELL THICKNESS CALCULATOR <200 ft Dia
API 653
© POWERS Engineering and Inspection, Inc. 2016
Appendix M
|  |  | Owner |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 0; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 10: Newest Bottom |  | Look up | [31 empty] | <45 | <=45 and <55 | >=55
|  |  | Location |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: San Antonio, TX; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 7: Cir (ft) |  | Joint Efficiency Based on Construction Date | [30 empty] | 200 | 0.91 | 0.88 | 0.92 |  | 0.957 | 0.974 | 0.955
|  |  | Tank Number |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 218; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 7: 106.8142 |  | API 650 6th |  | Suggested API standard |  |  |  | note: Use 85% for Tri-Pan Weld Inspection | [24 empty] | 300 | 0.88 | 0.81 | 0.87
|  |  | (D)iameter (ft) |  | 34 | gallons | BBLS | tons | lbs. |  |  | 0.85 |  | Suggested Welded Joint Eff. | [28 empty] | 400 | 0.85 | 0.75 | 0.83
|  |  | Shell Height (ft) |  | 30 | 203751.4737 | 4851.2256 | 714.072 | 1428144.0688 |  |  | Specific Gravity | [30 empty] | 500 | 0.8 | 0.7 | 0.79
|  |  | Fill (H)eight (ft) |  | 40 | 271668.6316 | 6468.3008 | 952.096 | 1904192.0918 | #REF! |  | JP-8 |  | Product Type
|  |  | Spec (G)ravity |  | 0.84 | 52.44 lbs/ft^3 | 7.01 lbs/gal |  |  | 0 |  | 0.84 |  | Suggested Specific Gravity
|  |  | Year Built |  | 1978 | Corrosion Allow (CA) |  | 0 |  | #REF!
|  |  | Operating Temp |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 100; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: API 650 Appendix M Temperature Modifier; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 7: 1
.
|  |  | API 653 | Height (H) | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: API 653 Joint Efficiency Table 4.2 Welded & 4.3 Rivet; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 8: Stress | Surplus | Next Inspection |  |  | Estimated or As built |  | Max G |  | Fill Height |  | API 653
|  |  |  | Shell | Product |  |  | Material | S | Actual | Thickness | Cor Rate | Next | Pass/ | Orig Thickness |  | Fill | Shell | Max Fill | Hydro | Hydro | Fill | Shell | Yield | Tensile |  | Weight of Shell | CG | Wt x CG
|  |  | Course | (in) | (ft) | Joint Type | E | Type | psi | (in) | (in) | in/year | years | Fail? | (in) | (in) | Height | Height | Given (g) | (g) = 1 | Stress | (ft) | (ft) | (psi) | (psi) |  | (lbs) | (ft) | (ft-lbs)
0 | 0 | 0 | Btm | 0 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 0
68.5714 | 5.7143 | 5.7143 | 1 | 68.5714 | 40 | 85% Butt Weld | 85% | A 36 | #REF! | 0.625 | #REF! | 0 | 15 + | Pass | 0.625 | 5/8 | #REF! | #REF! | #REF! | #REF! | #REF! | 40 | 30 | 36000 | 58000 | 5/8 | 15577.0636 | 2.8571 | 44505.8959
205.7143 | 17.1429 | 11.4286 | 2 | 137.1429 | 34.2857 | 85% Butt Weld | 85% | A 36 | #REF! | 0.5 | #REF! | 0 | 15 + | Pass | 0.5 | 0.5 | #REF! | #REF! | #REF! | #REF! | #REF! | 34.2857 | 24.2857 | 36000 | 58000 |  | 24923.3017 | 11.4286 | 284837.7339
411.4286 | 34.2857 | 17.1429 | 3 | 205.7143 | 22.8571 | 85% Butt Weld | 85% | A 36 | #REF! | 0.375 | #REF! | 0 | 15 + | Pass | 0.375 | 0.375 | #REF! | #REF! | #REF! | #REF! | #REF! | 22.8571 | 12.8571 | 36000 | 58000 |  | 28038.7144 | 25.7143 | 720995.514
685.7143 | 57.1429 | 22.8571 | 4 | 274.2857 | 5.7143 | 85% Butt Weld | 85% | A 36 | #REF! | 0.3125 | #REF! | 0 | 15 + | Pass | 0.3125 | 0.3125 | #REF! | - | #REF! | 30 | #REF! | 5.7143 | -4.2857 | 36000 | 58000 |  | 31154.1271 | 45.7143 | 1424188.6696
1028.5714 | 85.7143 | 28.5714 | 5 | 342.8571 | -17.1429 | 85% Butt Weld | 85% | A 36 | #REF! | 0.3125 | #REF! | 0 | 15 + | Pass | 0.3125 | 0.3125 | - | - | #REF! | 30 | #REF! | -17.1429 | -27.1429 | 36000 | 58000 |  | 38942.6589 | 71.4286 | 2781618.4954
1440 | 120 | 34.2857 | 6 | 411.4286 | -45.7143 | 85% Butt Weld | 85% | A 36 | #REF! | 0 | #REF! | 0 | 15 + | Pass | 0 | 0 | - | - | #REF! | 30 | #REF! | -45.7143 | -55.7143 | 36000 | 58000 |  | 0 | 102.8571 | 0
1920 | 160 | 40 | 7 | 480 | -80 | 85% Butt Weld | 85% | A 36 | #REF! | 0 | #REF! | 0 | 15 + | Pass | 0 | 0 | - | - | #REF! | 30 | #REF! | -80 | -90 | 36000 | 58000 |  | 0 | 140 | 0
1920 | 160 | 0 | 8 | 0 | - | 85% Butt Weld | 85% | A 36 | #REF! | 0 | - | 0 | 15 + | Pass | 0 | 0 | - | - | #REF! | 30 | #REF! | 0 | -130 | 36000 | 58000 |  | 0 | 160 | 0
1920 | 160 | 0 | 9 | 0 | - | 85% Butt Weld | 85% | A 36 | #REF! | 0 | - | 0 | 15 + | Pass | 0 | 0 | - | - | #REF! | 30 | #REF! | 0 | -130 | 36000 | 58000 |  | 0 | 160 | 0
1920 | 160 | 0 | 10 | 0 | - | 85% Butt Weld | 85% | A 36 | #REF! | 0 | - | 0 | 15 + |  | 0 | 0 | - | - | #REF! | 30 | #REF! | 0 | -130 | 36000 | 58000 |  | 0 | 160 | 0
| 160 | 0 | Top Angle | 0
|  | 160 | Sum | 160 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: (ft) | [6 empty] | #REF! | #REF! | #REF! | #REF! | [6 empty] | 138635.8658 | 37.9133 | 5256146.3088
|  | #REF! |  |  | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 10: #REF! | [16 empty] | 1.3188
|  |  | API 650 | Height | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: Corr; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 7: Allowable Stress |  | API 650 Fill Height
|  |  |  | Shell | Product | Joint | Allow | Design | Hydro | Hydro | Actual | Design | Hydro |  |  | Annular Plate API 650 5.5.3
|  |  | Course | (in) | (ft) | Type | in | psi | psi | (in) | (in) | (ft) | (ft) |  |  | 1st course stress
|  |  | 1 | 68.5714 | 40 | 0.85 | 0 | 23200 | 24900 | 0.13846 | 0.625 | #REF! | 180.5604 |  |  | Dsn | Hydro | Max | Thick | Width | Thickness
|  |  | 2 | 137.1429 | 34.2857 | 0.85 | 0 | 23200 | 24900 | 0.11817 | 0.5 | #REF! | 156.4968 |  |  | #REF! | #REF! | #REF! | 0.13846 |  | #REF!
|  |  | 3 | 205.7143 | 22.8571 | 0.85 | 0 | 23200 | 24900 | 0.077597 | 0.375 | #REF! | 127.6033
|  |  | 4 | 274.2857 | 5.7143 | 0.85 | 0 | 23200 | 24900 | 0.016737 | 0.3125 | #REF! | 140.9805
|  |  | 5 | 342.8571 | -17.1429 | 0.85 | 0 | 23200 | 24900 | -0.064411 | 0.3125 | #REF! | 140.3144
|  |  | 6 | 411.4286 | -45.7143 | 0.85 | 0 | 23200 | 24900 | -0.16585 | 0 | #REF! | #DIV/0!
|  |  | 7 | 480 | -80 | 0.85 | 0 | 23200 | 24900 | -0.28757 | 0 | #REF! | #DIV/0!
|  |  | 8 | #REF! | #REF! | 0.85 | 0 | 23200 | 24900 | #REF! | 0 | #REF! | #REF!
|  |  | Sum | #REF! | [6 empty] | Min | #REF! | #DIV/0!
|  |  | API 650 | Height | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: Corr; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 7: Allowable Stress
|  |  | Variable PT | Shell | Product | Joint | Allow | Design | Hydro | Hydro | Actual
|  |  | Course | (in) | (ft) | Type | in | psi | psi | (in) | (in)
|  |  | 1 | 68.5714 | 40 | 0.85 | 0 | 23200 | 24900 | 0.375 | 0.625
|  |  | 2 | 137.1429 | 34.2857 | 0.85 | 0 | 23200 | 24900 | 0.375 | 0.5
|  |  | 3 | 205.7143 | 22.8571 | 0.85 | 0 | 23200 | 24900 | #NUM! | 0.375
|  |  | 4 | 274.2857 | 5.7143 | 0.85 | 0 | 23200 | 24900 | #NUM! | 0.3125
|  |  | 5 | 342.8571 | -17.1429 | 0.85 | 0 | 23200 | 24900 | #NUM! | 0.3125
|  |  | 6 | 411.4286 | -45.7143 | 0.85 | 0 | 23200 | 24900 | #NUM! | 0
|  |  | 7 | 480 | -80 | 0.85 | 0 | 23200 | 24900 | #NUM! | 0
|  |  | 8 | #REF! | #REF! | 0.85 | 0 | 23200 | 24900 | #NUM! | 0
|  |  | Sum | #REF! | [6 empty] | Max
API 653
|  |  | Variable PT | Shell | Product | Joint | Allow | Design | Hydro | Hydro | Actual
|  |  | Course | (in) | (ft) | Type | in | psi | psi | (in) | (in)
|  |  | 1 | 68.5714 | 40 | 0.85 | 0 | #REF! | 24900 | 0.375 | 0.625
|  |  | 2 | 137.1429 | 34.2857 | 0.85 | 0 | #REF! | 24900 | 0.375 | 0.5
|  |  | 3 | 205.7143 | 22.8571 | 0.85 | 0 | #REF! | 24900 | #REF! | 0.375
|  |  | 4 | 274.2857 | 5.7143 | 0.85 | 0 | #REF! | 24900 | #REF! | 0.3125
|  |  | 5 | 342.8571 | -17.1429 | 0.85 | 0 | #REF! | 24900 | #REF! | 0.3125
|  |  | 6 | 411.4286 | -45.7143 | 0.85 | 0 | #REF! | 24900 | #REF! | 0
|  |  | 7 | 480 | -80 | 0.85 | 0 | #REF! | 24900 | #REF! | 0
|  |  | 8 | #REF! | -120 | 0.85 | 0 | 23200 | 24900 | #REF! | 0
|  |  | Sum | #REF! | [6 empty] | Max
API 653
|  |  | Actual thickness, t (in) | Top of course (ft) | Top to tank | E | Y (psi) | 0.80Y | 0.88Y | 0.472T | 0.519T | S (psi) | Sd (psi) |  | H = Design liquid level (ft) | h = Heigth of of course,(in) | r = Tank radius, (in) | L = (6/Dt)0.5 | L/H | CA | tpd w/o CA | tpd, tu, tdx (preliminary design - in) | t1d (design - in) | t1d (smaller of tpd, td - in) | h1/(rt1)0.5 |  | First Trial | K = (tL / tu) | C = ((K0.5(K-1))/(1+K1.5) | (rtu)^.5 | x1 = (0.61(rtu)0.5 + 3.84CH) | x2 = (12CH) | x3 = (1.22(rtu)0.5) | x = (smallest of x1, x2, x3) | tdx-CA | tdx | Second Trial | K = (tL / tu) | C = ((K0.5(K-1))/(1+K1.5) | x1 = (0.61(rtu)0.5 + 3.84CH) | x2 = (12CH) | x3 = (1.22(rtu)0.5) | x = (smallest of x1, x2, x3) | tdx |  | Third Trial | K = (tL / tu) | C = ((K0.5(K-1))/(1+K1.5) | x1 = (0.61(rtu)0.5 + 3.84CH) | x2 = (12CH) | x3 = (1.22(rtu)0.5) | x = (smallest of x1, x2, x3) | tdx = t2a | h1/(rt1)^0.5 | if 1.375<=h1/(rt1)^.5 then t2 = t1 | if h1/(rt1)^.5 >= 2.625 then t2 =t2a | if inbetween 1.375 and 2.625 then | Tmin | Min course thickness < 0.375 | CA
|  | 1 | 0.625 | 30 | 30 | 0.85 | 36000 | 28800 |  |  |  | 28800 | 24480 |  | 40 | 68.5714 | 204 | 0.53137 | 0.013284 | 0 | 0.10056 | 0.10056 | 0.10793 | 0.10056 | [33 empty] | 0.10056 | 0.375
|  | 2 | 0.5 | 24.2857 | 30 | 0.85 | 36000 | 28800 |  |  |  | 28800 | 24480 |  | 34.2857 | 137.1429 | 204 |  |  | 0 | 0.085822 | 0.085822 |  |  | 15.14 |  |  | 1.1717 | 0.081924 | 4.1842 | 13.3383 | 33.7061 | 5.1047 | 5.1047 | 0.10271 | 0.10271 |  | 0.97902 | -0.010543 | 1.4041 | -4.3378 | 5.5845 | -4.3378 | 0.1051 |  |  | 0.95679 | -0.021834 | -0.050162 | -8.9833 | 5.649 | -8.9833 | 0.10627 | 15.14 | 0.10056 | 0.10627 | 0.17167 | 0.10627 | 0.375
|  | 3 | 0.375 | 12.8571 | 30 | 0.85 | 36000 |  | 31680 | #REF! | #REF! | #REF! | #REF! |  | 22.8571 | 205.7143 | 204 |  |  | 0 | #REF! | #REF! |  |  | 29.4545 |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF!
|  | 4 | 0.3125 | -4.2857 | 30 | 0.85 | 36000 |  | 31680 | #REF! | #REF! | #REF! | #REF! |  | 0 | 274.2857 | 204 |  |  | 0 | #REF! | #REF! |  |  | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF!
|  | 5 | 0.3125 | -27.1429 | 30 | 0.85 | 36000 |  | 31680 | #REF! | #REF! | #REF! | #REF! |  | 0 | 342.8571 | 204 |  |  | 0 | #REF! | #REF! |  |  | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF!
|  | 6 | 0 | -55.7143 | 30 | 0.85 | 36000 |  | 31680 | #REF! | #REF! | #REF! | #REF! |  | 0 | 411.4286 | 204 |  |  | 0 | #REF! | #REF! |  |  | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF!
|  | 7 | 0 | -90 | 30 | 0.85 | 36000 |  | 31680 | #REF! | #REF! | #REF! | #REF! |  | 0 | 480 | 204 |  |  | 0 | #REF! | #REF! |  |  | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF!
|  | 8 | 0 | -130 | 30 | 0.85 | 36000 |  | 31680 | #REF! | #REF! | #REF! | #REF! |  | 0 | #REF! | 204 |  |  | 0 | #REF! | #REF! |  |  | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF!
API 650
|  |  | Actual thickness, t (in) | Top of course (ft) | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: Top to tank; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: E; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: Y (psi) |  | Sd (psi) | St (psi) |  | H = Design liquid level (ft) | h = Heigth of of course,(in) | r = Tank radius, (in) | L = (6/Dt)0.5 | L/H | CA | tpd w/o CA | tpd, tu, tdx (preliminary design - in) | t1d (design - in) | t1d (smaller of tpd, td - in) | h1/(rt1)0.5 |  | First Trial | K = (tL / tu) | C = ((K0.5(K-1))/(1+K1.5) | (rtu)^.5 | x1 = (0.61(rtu)0.5 + 3.84CH) | x2 = (12CH) | x3 = (1.22(rtu)0.5) | x = (smallest of x1, x2, x3) | tdx-CA | tdx | Second Trial | K = (tL / tu) | C = ((K0.5(K-1))/(1+K1.5) | x1 = (0.61(rtu)0.5 + 3.84CH) | x2 = (12CH) | x3 = (1.22(rtu)0.5) | x = (smallest of x1, x2, x3) | tdx |  | Third Trial | K = (tL / tu) | C = ((K0.5(K-1))/(1+K1.5) | x1 = (0.61(rtu)0.5 + 3.84CH) | x2 = (12CH) | x3 = (1.22(rtu)0.5) | x = (smallest of x1, x2, x3) | tdx = t2a | h1/(rt1)^0.5 | if 1.375<=h1/(rt1)^.5 then t2 = t1 | if h1/(rt1)^.5 >= 2.625 then t2 =t2a | if inbetween 1.375 and 2.625 then | Tmin | Min course thickness < 0.375 | CA
|  | 1 | 0.625 | 30 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 30; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.85; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: 36000 |  | 23200 | 24900 |  | 40 | 68.5714 | 204 | 0.33211 | 0.0083026 | 0 | 0.12483 | 0.12483 | 0.13379 | 0.12483 | [33 empty] | 0.12483 | 0.375
|  | 2 | 0.5 | 24.2857 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 30; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.85; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: 36000 |  | 23200 | 24900 |  | 34.2857 | 137.1429 | 204 |  |  | 0 | 0.10654 | 0.10654 |  |  | 13.5886 |  |  | 1.1717 | 0.081924 | 4.6619 | 13.6297 | 33.7061 | 5.6876 | 5.6876 | 0.10083 | 0.10083 |  | 1.238 | 0.11137 | 17.4291 | 45.8203 | 5.5332 | 5.5332 | 0.10087 |  |  | 1.2375 | 0.11116 | 17.4026 | 45.736 | 5.5342 | 5.5342 | 0.10087 | 13.5886 | 0.12483 | 0.10087 | -0.13999 | 0.10087 | 0.375
|  | 3 | 0.375 | 12.8571 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 30; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.85; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: 36000 |  | 23200 | 24900 |  | 22.8571 | 205.7143 | 204 |  |  | 0 | 0.069958 | 0.069958 | [5 empty] | 1.4419 | 0.19426 | 3.7778 | 19.3548 | 53.2823 | 4.6089 | 4.6089 | 0.067018 | 0.067018 |  | -2.0888 | #NUM! | #NUM! | #NUM! | 4.511 | #NUM! | #NUM! |  |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  |  |  | #NUM! | #NUM!
|  | 4 | 0.3125 | -4.2857 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 30; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.85; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: 36000 |  | 23200 | 24900 |  | 0 | 274.2857 | 204 |  |  | 0 | -0.0032007 | -0.0032007 | [5 empty] | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  |  |  | #NUM! | #NUM!
|  | 5 | 0.3125 | -27.1429 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 30; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.85; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: 36000 |  | 23200 | 24900 |  | 0 | 342.8571 | 204 |  |  | 0 | -0.0032007 | -0.0032007 | [5 empty] | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  |  |  | #NUM! | #NUM!
|  | 6 | 0 | -55.7143 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 30; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.85; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: 36000 |  | 23200 | 24900 |  | 0 | 411.4286 | 204 |  |  | 0 | -0.0032007 | -0.0032007 | [5 empty] | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  |  |  | #NUM! | #NUM!
|  | 7 | 0 | -90 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 30; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.85; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: 36000 |  | 23200 | 24900 |  | 0 | 480 | 204 |  |  | 0 | -0.0032007 | -0.0032007 | [5 empty] | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  |  |  | #NUM! | #NUM!
|  | 8 | 0 | -130 | ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 4: 30; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 5: 0.85; ASTM A6, Table 13, Permitted Variations from a flat surface (shell course heigh, ft) 6: 36000 |  | 23200 | 24900 |  | 0 | #REF! | 204 |  |  | 0 | -0.0032007 | -0.0032007 | [5 empty] | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! |  |  |  |  | #NUM! | #NUM!
Joint Effeciency Table
|  |  | 1 Lap Rivet | 0.45
|  |  | 2 Butt Rivet | 0.75
|  |  | 2 Lap Rivet | 0.6
|  |  | 3 Butt Rivet | 0.85
|  |  | 3 Lap Rivet | 0.7
|  |  | 4 Butt Rivet | 0.9
|  |  | 4 Lap Rivet | 0.75
|  |  | 5 Butt Rivet | 0.91
|  |  | 6 Butt Rivet | 0.92
|  |  | 70% Butt Weld | 0.7
|  |  | 85% Butt Weld | 0.85
|  |  | Bolted | 0.7
|  |  | Butt Weld 100% | 1
|  |  | Dbl Lap W | 0.7
|  |  | Sgle Lap Weld | 0.35
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 11 | 12 | 13 | 14 | 15
Materials Table
|  |  | 0.35 4: API 650; 0.35 6: API 653 | API 653 Hydro
| Group |  |  | YIELD | TENSILE | Sd | St | St | St | .472 T | Min 1st & 2nd | Min 3rd + | Rivet | Group | Min 1st & 2nd | Min 3rd +
| I |  | A 131 A | 34000 | 58000 | 22700 | 24900 | 27400 | 30100 | 27376 | #REF! | 27376 | 21000 | I | 27400 | 30100 |  | 30265.91
| II |  | A 131 B | 34000 | 58000 | 22700 | 24900 | 27400 | 30100 | 27376 | #REF! | 27376 | 21000 | II | 27400 | 30100 |  | 30265.91
| IIIA |  | A 131 CS | 34000 | 58000 | 22700 | 24900 | 27400 | 30100 | 27376 | #REF! | 27376 | 21000 | IIIA | 27400 | 30100 |  | 30265.91
| VI |  | A 131 EH36 | 51000 | 71000 | 28400 | 30400 | 33500 | 36800 | 33512 | #REF! | 33512 | 21000 | VI | 33500 | 36800 |  | 37865.72
| I |  | A 283 C | 30000 | 55000 | 20000 | 22500 | 26000 | 27000 | 25960 | #REF! | 25960 | 21000 | I | 26000 | 27000 |  | 26666
| I |  | A 285 C | 30000 | 55000 | 20000 | 22500 | 26000 | 27000 | 25960 | #REF! | 25960 | 21000 | I | 26000 | 27000 |  | 26666
| II |  | A 36 | 36000 | 58000 | 23200 | 24900 | 27400 | 30100 | 27376 | #REF! | 27376 | 21000 | II | 27400 | 30100 |  | 30932.56
| III |  | A 516 55 | 30000 | 55000 | 20000 | 22500 | 26000 | 27000 | 25960 | #REF! | 25960 | 21000 | III | 26000 | 27000 |  | 26666
| III |  | A 516 60 | 32000 | 60000 | 21300 | 24000 | 28200 | 28800 | 28320 | #REF! | 28320 | 21000 | III | 28200 | 28800 |  | 28399.29
| IV |  | A 516 65 | 35000 | 65000 | 23300 | 26300 | 30700 | 31500 | 30680 | #REF! | 30680 | 21000 | IV | 30700 | 31500 |  | 31065.89
| IV |  | A 516 70 | 38000 | 70000 | 25300 | 28500 | 33000 | 34200 | 33040 | #REF! | 33040 | 21000 | IV | 33000 | 34200 |  | 33732.49
| VI |  | A 537 1 | 50000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | #REF! | 33040 | 21000 | VI | 33000 | 36300 |  | 37332.4
| VI |  | A 537 2 | 60000 | 80000 | 32000 | 34300 | 37800 | 41500 | 37760 | #REF! | 37760 | 21000 | VI | 37800 | 41500 |  | 42665.6
| IIIA |  | A 573 58 | 32000 | 58000 | 21300 | 24000 | 27400 | 28800 | 27376 | #REF! | 27376 | 21000 | IIIA | 27400 | 28800 |  | 28399.29
| IV |  | A 573 65 | 35000 | 65000 | 23300 | 26300 | 30700 | 31500 | 30680 | #REF! | 30680 | 21000 | IV | 30700 | 31500 |  | 31065.89
| IV |  | A 573 70 | 42000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | #REF! | 33040 | 21000 | IV | 33000 | 36300 |  | 37332.4
| IV |  | A 622 B | 40000 | 65000 | 26000 | 27900 | 30700 | 33700 | 30680 | #REF! | 30680 | 21000 | IV | 30700 | 33700 |  | 34665.8
| IVA |  | A 622 C | 43000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | #REF! | 33040 | 21000 | IVA | 33000 | 36300 |  | 37332.4
| VI |  | A 633 C | 50000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | #REF! | 33040 | 21000 | VI | 33000 | 36300 |  | 37332.4
| VI |  | A 633 D | 50000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | #REF! | 33040 | 21000 | VI | 33000 | 36300 |  | 37332.4
| VI |  | A 678 A | 50000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | #REF! | 33040 | 21000 | VI | 33000 | 36300 |  | 37332.4
| VI |  | A 678 B | 60000 | 80000 | 32000 | 34300 | 37800 | 41500 | 37760 | #REF! | 37760 | 21000 | VI | 37800 | 41500 |  | 42665.6
| VI |  | A 737 B | 50000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | #REF! | 33040 | 21000 | VI | 33000 | 36300 |  | 37332.4
| VI |  | A 841 | 50000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | #REF! | 33040 | 21000 | VI | 33000 | 36300 |  | 37332.4
|  |  | B 209 Alclad 3003 | 18000 | 40000 | #REF! | #REF! | #REF! | #REF! | 18880 | #REF! | 18880 | [5 empty] | #REF!
|  |  | JIS G 3103 SS40 | 35534.2365 | 58015.08 |  |  |  |  | 27383.1178 | #REF! | 27383.1178
|  |  | JIS G 3115 SPV490 | 71068.473 | 97900.4475 |  |  |  |  | 46209.0112 | #REF! | 46209.0112
|  |  | SM50B | 42000 | 70000 | 28000 | 30000 | 33000 | 36300 | 33040 | 30030 | 33040 | 21000 |  |  |  |  | 37332.4
|  |  | SM 53CN | 50000 | 75000 | 28000 | 30000 | 33000 | 36300 | 35400 | 32175 | 35400 | 21000 |  |  |  |  | 37332.4
| I |  | Riveted Unknown | 30000 | 55000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | 21000 | I | 21000 | 21000 |  | 27999.3
| I |  | Welded Unknown | 30000 | 55000 | 20000 | 22500 | 26000 | 27000 | 25960 | 23600 | 25960 | 21000 | I | 26000 | 27000 |  | 26666
|  |  | Thickness Table | [5 empty] | "32nd
|  |  | 1 | 0 | 0.03125 |  | 0 | 0 | 0
|  |  | 2 | 0.03125 | 0.03125 |  | 1/17 | 0.03125 | 0.03125
|  |  | 3 | 0.0625 | 0.0625 |  | 1/16 | 0.0625 | 0.09375
|  |  | 4 | 0.09375 | 0.125 |  | 1/8 | 0.09375 | 0.125
|  |  | 5 | 0.125 | 0.125 |  | 1/8 | 0.125 | 0.15625
|  |  | 6 | 0.15625 | 0.15625 |  | 3/16 | 0.15625 | 0.1875
|  |  | 7 | 0.1875 | 0.1875 |  | 3/16 | 0.1875 | 0.21875
|  |  | 8 | 0.21875 | 0.21875 |  | 1/4 | 0.21875 | 0.25
|  |  | 9 | 0.25 | 0.25 |  | 1/4 | 0.25 | 0.28125
|  |  | 10 | 0.28125 | 0.28125 |  | 5/16 | 0.28125 | 0.3125
|  |  | 11 | 0.3125 | 0.3125 |  | 5/16 | 0.3125 | 0.34375
|  |  | 12 | 0.34375 | 0.34375 |  | 3/8 | 0.34375 | 0.375
|  |  | 13 | 0.375 | 0.375 |  | 3/8 | 0.375 | 0.40625
|  |  | 14 | 0.4 | 0.40625 |  | 7/16 | 0.40625 | 0.4375
|  |  | 15 | 0.4375 | 0.4375 |  | 7/16 | 0.4375 | 0.46875
|  |  | 16 | 0.46875 | 0.46875 |  | 1/2 | 0.46875 | 0.5
|  |  | 17 | 0.5 | 0.5 |  | 1/2 | 0.5 | 0.53125
|  |  | 18 | 0.53125 | 0.53125 |  | 9/16 | 0.53125 | 0.5625
|  |  | 19 | 0.5625 | 0.5625 |  | 9/16 | 0.5625 | 0.59375
|  |  | 20 | 0.59375 | 0.59375 |  | 5/8 | 0.59375 | 0.625
|  |  | 21 | 0.625 | 0.625 |  | 5/8 | 5/8 | 0.65625
|  |  | 22 | 0.65625 | 0.65625 |  | 11/16 | 0.65625 | 0.6875
|  |  | 23 | 0.6875 | 0.6875 |  | 11/16 | 11/16 | 0.71875
|  |  | 24 | 0.71875 | 0.71875 |  | 3/4 | 0.71875 | 0.75
|  |  | 25 | 0.75 | 0.75 |  | 3/4 | 3/4 | 0.78125
|  |  | 26 | 0.78125 | 0.78125 |  | 13/16 | 0.78125 | 0.8125
|  |  | 27 | 0.8125 | 0.8125 |  | 13/16 | 13/16 | 0.84375
|  |  | 28 | 0.84375 | 0.84375 |  | 3/4 | 0.84375 | 0.875
|  |  | 29 | 0.875 | 0.875 |  | 3/4 | 3/4 | 0.90625
|  |  | 30 | 0.90625 | 0.90625 |  | 15/16 | 0.90625 | 0.9375
|  |  | 31 | 0.9375 | 0.9375 |  | 15/16 | 15/16 | 0.96875
|  |  | 32 | 0.96875 | 0.96875 | 1 |  | 0.96875 | 1
|  |  | 33 | 1 | 1 | 1 |  | 1 | 1.0312
|  |  | 34 | 1.0312 | 1.0312 | 1 | 1/16 | 1.0312 | 1.0625
|  |  | 35 | 1.0625 | 1.0625 | 1 | 1/16 | 1 1/16 | 1.0938
|  |  | 36 | 1.0938 | 1.0938 | 1 | 1/8 | 1.0938 | 1.125
|  |  | 37 | 1.125 | 1.125 | 1 | 1/8 | 1 1/8 | 1.1562
|  |  | 38 | 1.1562 | 1.1562 | 1 | 3/16 | 1.1562 | 1.1875
|  |  | 39 | 1.1875 | 1.1875 | 1 | 3/16 | 1 3/16 | 1.2188
|  |  | 40 | 1.2188 | 1.2188 | 1 | 1/4 | 1.2188 | 1.25
|  |  | 41 | 1.25 | 1.25 | 1 | 1/4 | 1 1/4 | 1.2812
|  |  | 42 | 1.2812 | 1.2812 | 1 | 5/16 | 1.2812 | 1.3125
|  |  | 43 | 1.3125 | 1.3125 | 1 | 5/16 | 1 5/16 | 1.3438
|  |  | 44 | 1.3438 | 1.3438 | 1 | 3/8 | 1.3438 | 1.375
|  |  | 45 | 1.375 | 1.375 | 1 | 3/8 | 1 3/8 | 1.4062
|  |  | 46 | 1.4062 | 1.4062 | 1 | 7/16 | 1.4062 | 1.4375
|  |  | 47 | 1.4375 | 1.4375 | 1 | 7/16 | 1 7/16 | 1.4688
|  |  | 48 | 1.4688 | 1.4688 | 1 | 1/2 | 1.4688 | 1.5
|  |  | 49 | 1.5 | 1.5 | 1 | 1/2 | 1 1/2 | 1.5312
|  |  | 50 | 1.5312 | 1.5312 | 1 | 9/16 | 1.5312 | 1.5625
|  |  | 51 | 1.5625 | 1.5625 | 1 | 9/16 | 1 9/16 | 1.5938
|  |  | 52 | 1.5938 | 1.5938 | 1 | 5/8 | 1.5938 | 1.625
|  |  | 53 | 1.625 | 1.625 | 1 | 5/8 | 1 5/8 | 1.6562
|  |  | 54 | 1.6562 | 1.6562 | 1 | 11/16 | 1.6562 | 1.6875
|  |  | 55 | 1.6875 | 1.6875 | 1 | 11/16 | 1 11/16 | 1.7188
|  |  | 56 | 1.7188 | 1.7188 | 1 | 3/4 | 1.7188 | 1.75
|  |  | 57 | 1.75 | 1.75 | 1 | 3/4 | 1 3/4 | 1.7812
|  |  | 58 | 1.7812 | 1.7812 | 1 | 13/16 | 1.7812 | 1.8125
|  |  | 59 | 1.8125 | 1.8125 | 1 | 13/16 | 1 13/16 | 1.8438
|  |  | 60 | 1.8438 | 1.8438 | 1 | 3/4 | 1.8438 | 1.875
|  |  | 61 | 1.875 | 1.875 | 1 | 3/4 | 1 3/4 | 1.9062
|  |  | 62 | 1.9062 | 1.9062 | 1 | 15/16 | 1.9062 | 1.9375
|  |  | 63 | 1.9375 | 1.9375 | 1 | 15/16 | 1 15/16 | 1.9688
|  |  | 64 | 1.9688 | 1.9688 | 2 |  | 1.9688 | 2
|  |  | 65 | 2 | 2 | 2 |  | 2 | 2.0312
|  |  | 66 | 2.0312 | 2.0312 | 2 | 1/16 | 2.0312 | 2.0625
|  |  | 67 | 2.0625 | 2.0625 | 2 | 1/16 | 2 1/16 | 2.0938
|  |  | 68 | 2.0938 | 2.0938 | 2 | 1/8 | 2.0625 | 2.125
|  |  | 69 | 2.125 | 2.125 | 2 | 1/8 | 2 1/8 | 2.1562
|  |  | 70 | 2.1562 | 2.1562 | 2 | 3/16 | 2.1562 | 2.1875
|  |  | 71 | 2.1875 | 2.1875 | 2 | 3/16 | 2 3/16 | 2.2188
|  |  | 72 | 2.2188 | 2.2188 | 2 | 1/4 | 2.2188 | 2.25
|  |  | 73 | 2.25 | 2.25 | 2 | 1/4 | 2 1/4 | 2.2812
|  |  | 74 | 2.2812 | 2.2812 | 2 | 5/16 | 2.2812 | 2.3125
|  |  | 75 | 2.3125 | 2.3125 | 2 | 5/16 | 2 5/16 | 2.3438
|  |  | 76 | 2.3438 | 2.3438 | 2 | 3/8 | 2.3438 | 2.375
API Standards
|  |  | 1900 |  | Unknown | 0.35
|  |  | 1901 |  | Unknown | 0.35
|  |  | 1902 |  | Unknown | 0.35
|  |  | 1903 |  | Unknown | 0.35
|  |  | 1904 |  | Unknown | 0.35
|  |  | 1905 |  | Unknown | 0.35
|  |  | 1906 |  | Unknown | 0.35
|  |  | 1907 |  | Unknown | 0.35
|  |  | 1908 |  | Unknown | 0.35
|  |  | 1909 |  | Unknown | 0.35
|  |  | 1910 |  | Unknown | 0.35
|  |  | 1911 |  | Unknown | 0.35
|  |  | 1912 |  | Unknown | 0.35
|  |  | 1913 |  | Unknown | 0.35
|  |  | 1914 |  | Unknown | 0.35
|  |  | 1915 |  | Unknown | 0.35
|  |  | 1916 |  | Unknown | 0.35
|  |  | 1917 |  | Unknown | 0.35
|  |  | 1918 |  | Unknown | 0.35
|  |  | 1919 |  | Unknown | 0.35
|  |  | 1920 |  | Unknown | 0.35
|  |  | 1921 |  | Unknown | 0.35
|  |  | 1922 |  | Unknown | 0.35
|  |  | 1923 |  | Unknown | 0.35
|  |  | 1924 |  | Unknown | 0.35
|  |  | 1925 |  | Unknown | 0.35
|  |  | 1926 |  | Unknown | 0.35
|  |  | 1927 |  | Unknown | 0.35
|  |  | 1928 |  | Unknown | 0.35
|  |  | 1929 |  | Unknown | 0.35
|  |  | 1930 |  | Unknown | 0.35
|  |  | 1931 |  | Unknown | 0.35
|  |  | 1932 |  | Unknown | 0.35
|  |  | 1933 |  | Unknown | 0.35
|  |  | 1934 |  | Unknown | 0.35
|  |  | 1935 |  | Unknown | 0.35
|  |  | 1936 |  | Unknown | 0.35
|  |  | 1937 |  | Unknown | 0.35
|  |  | 1938 |  | Unknown | 0.35
|  |  | 1939 |  | API 12C 1st | 0.7
|  |  | 1940 |  | API 12C 1st | 0.7
|  |  | 1941 |  | API 12C 1st | 0.7
|  |  | 1942 |  | API 12C 2nd | 0.7
|  |  | 1943 |  | API 12C 2nd | 0.7
|  |  | 1944 |  | API 12C 2nd | 0.7
|  |  | 1945 |  | API 12C 3rd | 0.7
|  |  | 1946 |  | API 12C 3rd | 0.7
|  |  | 1947 |  | API 12C 4th | 0.7
|  |  | 1948 |  | API 12C 5th | 0.7
|  |  | 1949 |  | API 12C 6th | 0.7
|  |  | 1950 |  | API 12C 7th | 0.7
|  |  | 1951 |  | API 12C 8th | 0.7
|  |  | 1952 |  | API 12C 9th | 0.7
|  |  | 1953 |  | API 12C 10th | 0.7
|  |  | 1954 |  | API 12C 11th | 0.7
|  |  | 1955 |  | API 12C 12th | 0.7
|  |  | 1956 |  | API 12C 13th | 0.7
|  |  | 1957 |  | API 12C 14th | 0.7
|  |  | 1958 |  | API 12C 15th | 0.85
|  |  | 1959 |  | API 12C 15th | 0.85
|  |  | 1960 |  | API 12C 15th | 0.85
|  |  | 1961 |  | API 650 1st | 0.85
|  |  | 1962 |  | API 650 1st | 0.85
|  |  | 1963 |  | API 650 2nd | 0.85
|  |  | 1964 |  | API 650 2nd | 0.85
|  |  | 1965 |  | API 650 2nd | 0.85
|  |  | 1966 |  | API 650 3rd | 0.85
|  |  | 1967 |  | API 650 3rd | 0.85
|  |  | 1968 |  | API 650 3rd | 0.85
|  |  | 1969 |  | API 650 4th | 0.85
|  |  | 1970 |  | API 650 4th | 0.85
|  |  | 1971 |  | API 650 4th | 0.85
|  |  | 1972 |  | API 650 5th | 0.85
|  |  | 1973 |  | API 650 5th | 0.85
|  |  | 1974 |  | API 650 6th | 0.85
|  |  | 1975 |  | API 650 6th | 0.85
|  |  | 1976 |  | API 650 6th | 0.85
|  |  | 1977 |  | API 650 6th | 0.85
|  |  | 1978 |  | API 650 6th | 0.85
|  |  | 1979 |  | API 650 7th | 0.85
|  |  | 1980 |  | API 650 7th | 1
|  |  | 1981 |  | API 650 7th | 1
|  |  | 1982 |  | API 650 7th | 1
|  |  | 1983 |  | API 650 7th | 1
|  |  | 1984 |  | API 650 8th | 1
|  |  | 1985 |  | API 650 8th | 1
|  |  | 1986 |  | API 650 8th | 1
|  |  | 1987 |  | API 650 8th | 1
|  |  | 1988 |  | API 650 8th | 1
|  |  | 1989 |  | API 650 8th | 1
|  |  | 1990 |  | API 650 8th | 1
|  |  | 1991 |  | API 650 9th | 1
|  |  | 1992 |  | API 650 9th | 1
|  |  | 1993 |  | API 650 9th | 1
|  |  | 1994 |  | API 650 9th | 1
|  |  | 1995 |  | API 650 9th | 1
|  |  | 1996 |  | API 650 9th | 1
|  |  | 1997 |  | API 650 9th | 1
|  |  | 1998 |  | API 650 9th | 1
|  |  | 1999 |  | API 650 10th | 1
|  |  | 2000 |  | API 650 10th | 1
|  |  | 2001 |  | API 650 10th | 1
|  |  | 2002 |  | API 650 10th | 1
|  |  | 2003 |  | API 650 10th | 1
|  |  | 2004 |  | API 650 10th | 1
|  |  | 2005 |  | API 650 10th | 1
|  |  | 2006 |  | API 650 10th | 1
|  |  | 2007 |  | API 650 11th | 1
|  |  | 2008 |  | API 650 11th | 1
|  |  | 2009 |  | API 650 11th | 1
|  |  | 2010 |  | API 650 11th | 1
|  |  | 2011 |  | API 650 11th | 1
|  |  | 2012 |  | API 650 11th | 1
|  |  | 2013 |  | API 650 11th | 1
|  |  | 2014 |  | API 650 11th | 1
|  |  | 2015 |  | API 650 11th | 1
|  |  | 2016 |  | API 650 11th | 1
|  |  | 2017 |  | API 650 11th | 1
|  |  | 2018 |  | API 650 11th | 1
|  |  | 2019 |  | API 650 11th | 1
|  |  | 2020 |  | API 650 11th | 1
|  |  | Product | Specific Gravity | Vapor Pressure | Flash Point (F)
|  |  | 6 Fuel Oil | 1.08 | 1 | 200
|  |  | Asphalt | 1.08 | 0 | 200
|  |  | Av Gas | 0.7 | 150 | -20
|  |  | Bio Diesel | 0.87 | 0.4 | 100
|  |  | Caustic | 1.5 | 0 | 200
|  |  | Crude | 0.92 | 1 | 150
|  |  | Diesel | 0.82 | 0.4 | 150
|  |  | Diesel Low Sulfur | 0.86 | 0 | 150
|  |  | Diesel Marine F-76 | 0.86 | 0 | 140
|  |  | Ethanol | 0.79 | 130 | -20
|  |  | E-85 | 0.78 | 12 | -20
|  |  | F-76 | 0.8418 | 3 | 140
|  |  | Fertilizer | 1.5 | 0 | 200
|  |  | Fertilizer UAN 32 | 1.33 | 0 | 200
|  |  | Fuel Oil | 0.97 | 1 | 200
|  |  | Gas Oil | 0.82 | 130 | -20
|  |  | Gasoline | 0.72 | 130 | -20
|  |  | Jet | 0.82 | 3 | 140
|  |  | JP-4 | 0.79 | 3 | -20
|  |  | JP-5 | 0.845 | 3 | 140
|  |  | JP-8 | 0.84 | 3 | 100
|  |  | Kersone | 0.82 | 0.5 | 100
|  |  | Lignin | 1.25 | 0 | 200
|  |  | Naptha | 0.701 | 0.5 | 100
|  |  | Rerun Alkylate | 0.699 | 0 | 200
|  |  | Sulfuric Acid | 1.85 | 0 | 200
|  |  | Waste Water | 1 | 0 | 200
|  |  | Water | 1 | 0 | 200
|  |  | Wax | 1.05 | 0 | 200
|  |  |  | 1 | 0 | 200
Annular Plates API 650 table 5.1b
|  |  |  | 27 | 30 | 32 | 36
|  |  | 0 | 0.236 | 0.236 | 0.28125 | 0.34375
|  |  | 0.75 | 0.236 | 0.236 | 0.28125 | 0.34375
|  |  | 1 | 0.236 | 0.28125 | 0.375 | 0.4375
|  |  | 1.25 | 0.236 | 0.34375 | 0.46875 | 0.5625 |  | Dsn | Width | Thickness
|  |  | 1.5 | 0.3125 | 0.4375 | 0.5625 | 0.6875 |  | #REF! | #REF! | #REF!
|  |  | 1.75 | 0.34375 | 0.5 | 0.625 | 0.75
|  |  | 0 | 0.24
|  |  | 27 | #REF!
|  |  | 30 | #REF!
|  |  | 32 | #REF!
|  |  | 36 | #REF!

## Shell Data
|  | angle | 0.7634° | 2.29° | 3.817° | 5.344° | 6.871° | 8.397° | 9.924° | 11.45° | 12.98° | 14.5° | 16.03° | 17.56° | 19.09° | 20.61° | 22.14° | 23.67° | 25.19° | 26.72° | 28.25° | 29.77° | 31.3° | 32.83° | 34.35° | 35.88° | 37.41° | 38.93° | 40.46° | 41.99° | 43.51° | 45.04° | 46.57° | 48.09° | 49.62° | 51.15° | 52.68° | 54.2° | 55.73° | 57.26° | 58.78° | 60.31° | 61.84° | 63.36° | 64.89° | 66.42° | 67.94° | 69.47° | 71° | 72.52° | 74.05° | 75.58° | 77.1° | 78.63° | 80.16° | 81.68° | 83.21° | 84.74° | 86.27° | 87.79° | 89.32° | 90.85° | 92.37° | 93.9° | 95.43° | 96.95° | 98.48° | 100° | 101.5° | 103.1° | 104.6° | 106.1° | 107.6° | 109.2° | 110.7° | 112.2° | 113.7° | 115.3° | 116.8° | 118.3° | 119.9° | 121.4° | 122.9° | 124.4° | 126° | 127.5° | 129° | 130.5° | 132.1° | 133.6° | 135.1° | 136.7° | 138.2° | 139.7° | 141.2° | 142.8° | 144.3° | 145.8° | 147.3° | 148.9° | 150.4° | 151.9° | 153.4° | 155° | 156.5° | 158° | 159.6° | 161.1° | 162.6° | 164.1° | 165.7° | 167.2° | 168.7° | 170.2° | 171.8° | 173.3° | 174.8° | 176.3° | 177.9° | 179.4° | 180.9° | 182.5° | 184° | 185.5° | 187° | 188.6° | 190.1° | 191.6° | 193.1° | 194.7° | 196.2° | 197.7° | 199.2° | 200.8° | 202.3° | 203.8° | 205.4° | 206.9° | 208.4° | 209.9° | 211.5° | 213° | 214.5° | 216° | 217.6° | 219.1° | 220.6° | 222.2° | 223.7° | 225.2° | 226.7° | 228.3° | 229.8° | 231.3° | 232.8° | 234.4° | 235.9° | 237.4° | 238.9° | 240.5° | 242° | 243.5° | 245.1° | 246.6° | 248.1° | 249.6° | 251.2° | 252.7° | 254.2° | 255.7° | 257.3° | 258.8° | 260.3° | 261.8° | 263.4° | 264.9° | 266.4° | 268° | 269.5° | 271° | 272.5° | 274.1° | 275.6° | 277.1° | 278.6° | 280.2° | 281.7° | 283.2° | 284.8° | 286.3° | 287.8° | 289.3° | 290.9° | 292.4° | 293.9° | 295.4° | 297° | 298.5° | 300° | 301.5° | 303.1° | 304.6° | 306.1° | 307.7° | 309.2° | 310.7° | 312.2° | 313.8° | 315.3° | 316.8° | 318.3° | 319.9° | 321.4° | 322.9° | 324.4° | 326° | 327.5° | 329° | 330.6° | 332.1° | 333.6° | 335.1° | 336.7° | 338.2° | 339.7° | 341.2° | 342.8° | 344.3° | 345.8° | 347.4° | 348.9° | 350.4° | 351.9° | 353.5° | 355° | 356.5°
|  | arc length/height | 12 | 36 | 60 | 84 | 108 | 132 | 156 | 180 | 204 | 228 | 252 | 276 | 300 | 324 | 348 | 372 | 396 | 420 | 444 | 468 | 492 | 516 | 540 | 564 | 588 | 612 | 636 | 660 | 684 | 708 | 732 | 756 | 780 | 804 | 828 | 852 | 876 | 900 | 924 | 948 | 972 | 996 | 1020 | 1044 | 1068 | 1092 | 1116 | 1140 | 1164 | 1188 | 1212 | 1236 | 1260 | 1284 | 1308 | 1332 | 1356 | 1380 | 1404 | 1428 | 1452 | 1476 | 1500 | 1524 | 1548 | 1572 | 1596 | 1620 | 1644 | 1668 | 1692 | 1716 | 1740 | 1764 | 1788 | 1812 | 1836 | 1860 | 1884 | 1908 | 1932 | 1956 | 1980 | 2004 | 2028 | 2052 | 2076 | 2100 | 2124 | 2148 | 2172 | 2196 | 2220 | 2244 | 2268 | 2292 | 2316 | 2340 | 2364 | 2388 | 2412 | 2436 | 2460 | 2484 | 2508 | 2532 | 2556 | 2580 | 2604 | 2628 | 2652 | 2676 | 2700 | 2724 | 2748 | 2772 | 2796 | 2820 | 2844 | 2868 | 2892 | 2916 | 2940 | 2964 | 2988 | 3012 | 3036 | 3060 | 3084 | 3108 | 3132 | 3156 | 3180 | 3204 | 3228 | 3252 | 3276 | 3300 | 3324 | 3348 | 3372 | 3396 | 3420 | 3444 | 3468 | 3492 | 3516 | 3540 | 3564 | 3588 | 3612 | 3636 | 3660 | 3684 | 3708 | 3732 | 3756 | 3780 | 3804 | 3828 | 3852 | 3876 | 3900 | 3924 | 3948 | 3972 | 3996 | 4020 | 4044 | 4068 | 4092 | 4116 | 4140 | 4164 | 4188 | 4212 | 4236 | 4260 | 4284 | 4308 | 4332 | 4356 | 4380 | 4404 | 4428 | 4452 | 4476 | 4500 | 4524 | 4548 | 4572 | 4596 | 4620 | 4644 | 4668 | 4692 | 4716 | 4740 | 4764 | 4788 | 4812 | 4836 | 4860 | 4884 | 4908 | 4932 | 4956 | 4980 | 5004 | 5028 | 5052 | 5076 | 5100 | 5124 | 5148 | 5172 | 5196 | 5220 | 5244 | 5268 | 5292 | 5316 | 5340 | 5364 | 5388 | 5412 | 5436 | 5460 | 5484 | 5508 | 5532 | 5556 | 5580 | 5604
Height from btm (ft) | Height from scanner (ft) | arc length/height (in.)
0 |  | 12 | -6.3809 | -6.383 | -6.8058 | -6.0291 | -6.3078 | -6.6064 | -7.1112 | -7.5904 | -7.6529 | -7.8084 | -8.057 | -8.3819 | -8.3075 | -8.1214 | -8.2503 | -8.3099 | -8.1828 | -7.9864 | -7.9198 | -7.9603 | -8.1661 | -8.1574 | -7.5485 | -6.9282 | -6.3699 | -5.6486 | -4.8626 | -4.2421 | -3.8201 | -3.4801 | -2.9526 | -2.3886 | -2.3275 | -2.2334 | -1.9855 | -1.5419 | -1.612 | -1.7111 | -1.6011 | -1.2434 | -1.086 | -0.99739 | -0.8939 | -0.7236 | -0.74543 | -0.77257 | -0.84076 | -0.82439 | -0.70896 | -0.44414 | -0.32382 | -0.148 | -0.015453 | 0.12591 | 0.17521 | 0.097427 | 0.082452 | 0.15588 | 0.34496 | 0.50849 | 0.43445 | 0.41368 | 0.37879 | 0.27345 | 0.12588 | -0.03169 | 0.017613 | 0.027364 | 0.16109 | 0.22847 | 0.23768 | 0.39927 | -0.87458 | -2.4547 | -1.7418 | -3.4861 | -3.751 | empty | -3.0628 | -6.3974 | -3.7737 | -0.43031 | -0.98771 | -1.9733 | -0.1915 | -0.22366 | 0.24161 | 0.42664 | 0.47813 | 1.0403 | 0.98054 | 1.0653 | 0.89035 | 1.2112 | 2.4279 | 2.4459 | 2.5306 | 2.4246 | 2.7968 | 2.7727 | 2.8277 | 2.5139 | 1.9271 | 1.917 | 1.5185 | 1.2063 | 0.73742 | 0.18301 | -0.46433 | -1.3898 | -2.2918 | -2.1259 | -2.0104 | -1.8883 | -1.9144 | -2.1337 | -2.0466 | -2.1651 | -2.2332 | -2.3252 | -2.4049 | -2.5822 | -2.6336 | -2.5367 | -2.227 | -2.176 | -2.9902 | -3.2837 | -2.8154 | -2.3263 | -1.9532 | -1.5526 | -1.5594 | -1.6108 | -1.8412 | -2.0854 | -2.3567 | -2.5962 | -2.729 | -2.8307 | -2.8269 | -2.8167 | -2.8449 | -2.9292 | -2.8598 | -2.1522 | -1.5595 | -1.2296 | -0.19435 | -0.057477 | 0.35478 | 0.41756 | -0.73713 | -2.7224 | -2.9258 | -3.0026 | -2.7438 | -2.3773 | -2.9134 | -2.4504 | -2.1801 | -1.4589 | -0.68641 | -2.3663 | -2.393 | -2.4297 | -0.81524 | -1.1895 | -1.1802 | -0.2342 | -0.22437 | -0.30662 | -0.10288 | -0.092184 | 0.56122 | 0.758 | 1.0956 | 0.74903 | 0.47831 | 0.34726 | 0.70768 | 0.59378 | 0.38986 | 0.25957 | 0.42087 | 0.41505 | 0.72446 | 0.87987 | 0.80837 | 0.7964 | 0.66651 | 0.54946 | 0.44295 | 0.24961 | 0.27035 | -0.6009 | -1.0961 | -1.7046 | -2.4511 | -1.7913 | -2.3429 | -2.5571 | -2.3786 | -2.5118 | -2.2352 | -1.9716 | -1.1899 | -1.5773 | -2.2123 | -1.6188 | -3.1018 | -3.5724 | -4.0936 | -4.1724 | -4.0341 | -3.6847 | -3.8241 | -4.1666 | -4.2213 | -4.1823 | -3.9509 | -2.1975 | -2.2333 | -3.9669 | -3.1148 | -2.4858 | -4.423 | -4.9092 | -5.4011 | -2.9168 | -2.9332 | -3.9588 | -3.1198 | -4.6254
|  | 36 | -1.5287 | -5.3601 | -5.5415 | -1.2132 | -1.2111 | -1.3848 | -1.634 | -1.8815 | -2.0011 | -2.0291 | -2.0118 | -1.9435 | -1.7644 | -1.6176 | -1.622 | -1.5836 | -1.5557 | -1.4724 | -1.5516 | -1.5782 | -1.5163 | -1.3888 | -1.3877 | -1.5219 | -1.5569 | -1.5549 | -1.4724 | -1.4187 | -1.3921 | -1.377 | -1.2538 | -1.135 | -1.0528 | -0.93219 | -0.96521 | -0.86692 | -0.92516 | -1.0277 | -0.95999 | -0.76872 | -0.59508 | -0.55738 | -0.4757 | -0.31949 | -0.23194 | -0.2003 | -0.1853 | -0.15864 | -0.0052028 | 0.16783 | 0.34913 | 0.49741 | 0.62034 | 0.75793 | 0.7455 | 0.66638 | 0.63308 | 0.68144 | 0.88398 | 1.1094 | 0.96861 | 1.0223 | 0.9788 | 0.92581 | 0.7745 | 0.64154 | 0.60051 | 0.59495 | 0.6243 | 0.59092 | 0.51751 | 0.39387 | 0.18727 | -0.43835 | -0.34695 | -0.23102 | -0.062554 | 0.71874 | -1.2766 | 0.29845 | -0.7013 | -1.1135 | -1.6702 | -2.7664 | 0.55848 | -0.10733 | -0.56227 | -5.2681 | 0.11009 | 1.8963 | 1.7401 | 1.8868 | 1.7286 | 1.69 | 2.1039 | 2.1216 | 2.2392 | 2.3948 | 2.5646 | 2.6854 | 2.7393 | 2.753 | 2.8059 | 2.8471 | 2.9271 | 3.0397 | 3.1428 | 3.3018 | 3.3694 | 3.4499 | 3.4814 | 3.5379 | 3.617 | 3.6548 | 3.5667 | 3.4236 | 3.2887 | 3.1276 | 2.9159 | 2.7321 | 2.6231 | 2.5445 | 2.5145 | 2.4798 | 2.4294 | 1.7663 | -0.3162 | 2.2877 | 2.4217 | 1.569 | 2.2823 | 3.169 | 3.2126 | 3.1455 | 3.0055 | 2.7136 | 2.3703 | 2.1136 | 1.9609 | 2.0267 | 2.0441 | 2.147 | 2.1405 | 2.1417 | 2.034 | 1.9574 | 1.9708 | 2.0806 | 2.3181 | 2.5266 | 2.5664 | 2.5111 | 1.3045 | 1.9548 | 1.6489 | 1.5089 | 1.4472 | 1.4649 | 1.5613 | 1.6342 | 1.6139 | 1.6077 | 1.6787 | 1.6595 | 1.6707 | 1.7848 | 1.5517 | 2.1104 | 2.0415 | 1.99 | 1.8343 | 1.6167 | 1.4869 | 1.3488 | 1.2308 | 1.1506 | 1.0848 | 1.0279 | 0.89963 | 0.81709 | 0.71426 | 0.50488 | 0.4578 | 0.4512 | 0.47984 | 0.48357 | 0.48343 | 0.43354 | 0.36264 | 0.30456 | 0.23638 | 0.13113 | 0.10505 | 0.077377 | 0.02124 | -0.064823 | -0.2144 | -0.34642 | -0.39395 | -0.56624 | -0.69188 | -0.84255 | -0.83448 | -0.78431 | -0.78109 | -0.80771 | -0.86301 | -0.99241 | -1.157 | -1.3023 | -1.4871 | -1.5681 | -1.5005 | -1.4637 | -1.4588 | -1.6168 | -1.5097 | -1.5448 | -1.4642 | -1.5474 | -1.5473 | -1.5862 | -1.6513 | -1.7425 | -1.8374 | -1.8963 | -1.9455 | -2.0277 | -2.0522 | -2.0524 | -1.8014 | -1.6038 | -1.488 | -1.4612
|  | 84 | 0.78985 | 0.90879 | 1.0171 | 1.0658 | 0.6301 | 0.021276 | -0.58212 | -1.238 | -1.7889 | -2.0293 | -2.0664 | -1.9245 | -1.7826 | -1.6672 | -1.6862 | -1.7214 | -1.7786 | -1.7611 | -1.7102 | -1.6795 | -1.6474 | -1.6354 | -1.753 | -1.7777 | -1.6254 | -1.5796 | -1.5312 | -1.5016 | -1.4975 | -1.4718 | -1.3966 | -1.2991 | -1.16 | -1.0338 | -0.98832 | -0.86578 | -0.84543 | -0.87476 | -0.87084 | -0.87293 | -0.8099 | -0.84481 | -0.8075 | -0.74538 | -0.61011 | -0.50315 | -0.39852 | -0.30225 | -0.16052 | 0.0027184 | 0.16244 | 0.32629 | 0.45948 | 0.57785 | 0.6195 | 0.61916 | 0.64308 | 0.65722 | 0.79825 | 0.97591 | 1.0228 | 1.0606 | 1.0521 | 1.0517 | 0.9545 | 0.79219 | 0.68142 | 0.61449 | 0.51565 | 0.32044 | 0.087179 | -0.17122 | -0.61012 | -0.78115 | -0.83522 | -0.78475 | -0.47167 | 0.024909 | 0.13858 | 0.52187 | 0.94315 | 1.3142 | 1.5075 | 1.7274 | 1.845 | 2.0175 | 1.9844 | 1.8837 | 1.7583 | 1.5592 | 1.4797 | 1.476 | 1.5263 | 0.96781 | 1.5548 | 1.5808 | 1.7054 | 1.889 | 2.132 | 2.3355 | 2.4431 | 2.5067 | 2.5518 | 2.6122 | 2.6594 | 2.7684 | 2.9597 | 3.2066 | 3.5028 | 3.7076 | 3.8115 | 3.8507 | 3.7875 | 3.6586 | 3.4314 | 3.1642 | 2.884 | 2.582 | 2.3217 | 2.0955 | 1.9251 | 1.7723 | 1.6539 | 1.061 | -1.1132 | 1.6062 | 1.7791 | 1.9525 | 2.1592 | -0.26405 | 2.6642 | 2.9 | 2.9193 | 2.8469 | 2.6627 | 2.4186 | 2.1628 | 2.0188 | 1.8507 | 1.767 | 1.677 | 1.6753 | 1.6124 | 1.5598 | 1.4991 | 1.6483 | 1.7599 | 1.9098 | 2.0301 | 2.1461 | 2.2079 | 2.1823 | 1.3517 | 1.8788 | 1.7246 | 1.6289 | 1.5959 | 1.5244 | 1.4459 | 1.389 | 1.4146 | 1.4557 | 1.5408 | 1.7913 | 1.9811 | 2.1503 | 2.283 | 2.3241 | 2.2632 | 2.0697 | 1.8137 | 1.5595 | 1.3133 | 1.1249 | 0.99429 | 0.90343 | 0.81586 | 0.76952 | 0.7293 | 0.69366 | 0.64374 | 0.63213 | 0.65675 | 0.69081 | 0.67796 | 0.62543 | 0.51321 | 0.3834 | 0.25917 | 0.18049 | 0.10082 | 0.029271 | -0.016567 | -0.073605 | -0.16197 | -0.24508 | -0.33456 | -0.36418 | -0.32465 | -0.27125 | -0.2769 | -0.32257 | -0.35631 | -0.42307 | -0.55719 | -0.7618 | -0.93111 | -1.1136 | -1.2995 | -1.4402 | -1.8637 | -1.592 | -1.604 | -1.6106 | -1.5666 | -1.511 | -1.3584 | -1.1769 | -1.0221 | -0.92065 | -0.83702 | -0.80452 | -0.84943 | -0.95966 | -1.1024 | -1.2594 | -1.4318 | -1.5931 | -1.6789 | -1.5174 | -1.2615 | -0.76124 | -0.20349 | 0.20875
|  | 108 | 1.7545 | 1.9816 | 2.0421 | 1.8591 | 1.3642 | 0.71461 | -0.060886 | -0.88608 | -1.6232 | -2.002 | -2.0834 | -1.9249 | -1.7688 | -1.6333 | -1.6223 | -1.6347 | -1.6709 | -1.6926 | -1.5905 | -1.5659 | -1.5567 | -1.6052 | -1.7559 | -1.7241 | -1.5027 | -1.4481 | -1.4167 | -1.3872 | -1.3921 | -1.3612 | -1.3142 | -1.2094 | -1.0618 | -0.89749 | -0.91983 | -0.66982 | -0.5884 | -0.62927 | -0.6383 | -0.70444 | -0.72216 | -0.76173 | -0.74078 | -0.71577 | -0.6147 | -0.50556 | -0.37469 | -0.23581 | -0.080822 | 0.10293 | 0.2508 | 0.4221 | 0.55337 | 0.68111 | 0.76429 | 0.8059 | 0.85163 | 0.82269 | 0.90319 | 1.0866 | 1.23 | 1.3067 | 1.2937 | 1.2692 | 1.1727 | 1.0048 | 0.89652 | 0.78094 | 0.63278 | 0.38208 | 0.083335 | -0.24385 | -0.75132 | -0.90016 | -1.0152 | -1.0033 | -0.7202 | -0.24297 | 0.19763 | 0.50651 | 0.83569 | 1.0436 | 1.2869 | 1.5227 | 1.6494 | 1.759 | 1.743 | 1.6643 | 1.5216 | 1.2986 | 1.3055 | 1.3666 | 1.3549 | 0.85592 | 1.4301 | 1.4382 | 1.5507 | 1.7397 | 2.0225 | 2.2968 | 2.4596 | 2.5423 | 2.5884 | 2.6509 | 2.6799 | 2.8069 | 3.0007 | 3.2861 | 3.7131 | 4.0178 | 4.1259 | 4.1478 | 4.034 | 3.8214 | 3.4866 | 3.142 | 2.8184 | 2.4545 | 2.1619 | 1.9016 | 1.7194 | 1.5447 | 0.83356 | -1.3344 | 1.2519 | 1.4511 | 1.727 | 1.9771 | 2.2331 | 1.58 | 2.7475 | 2.956 | 2.9392 | 2.8318 | 2.6245 | 2.4089 | 2.1962 | 2.0423 | 1.8885 | 1.7761 | 1.6545 | 1.5593 | 1.4615 | 1.3794 | 1.4238 | 1.6457 | 1.8235 | 1.99 | 2.084 | 2.1945 | 2.2381 | 2.1845 | 1.3907 | 1.8674 | 1.7519 | 1.6541 | 1.6024 | 1.4749 | 1.3613 | 1.2663 | 1.2365 | 1.2496 | 1.4056 | 1.8333 | 2.1404 | 2.336 | 2.4663 | 2.4712 | 2.3691 | 2.1477 | 1.8603 | 1.5655 | 1.277 | 1.0767 | 0.92278 | 0.82539 | 0.74069 | 0.68428 | 0.65431 | 0.61836 | 0.62939 | 0.79873 | 0.92147 | 0.95848 | 0.94369 | 0.84184 | 0.69837 | 0.5129 | 0.33589 | 0.25407 | 0.16067 | 0.099471 | 0.046804 | -0.011934 | -0.10501 | -0.17706 | -0.20572 | -0.18086 | -0.031012 | 0.10655 | 0.15022 | 0.12117 | 0.025379 | -0.12135 | -0.37025 | -0.64398 | -0.87545 | -1.0756 | -1.2461 | -1.3899 | -1.5426 | -1.5323 | -1.5471 | -1.5636 | -1.5076 | -1.3872 | -1.1909 | -0.8953 | -0.67288 | -0.56317 | -0.47345 | -0.45759 | -0.49885 | -0.62901 | -0.80974 | -1.0281 | -1.2577 | -1.4576 | -1.5642 | -1.4244 | -1.009 | -0.33239 | 0.39818 | 0.97567
|  | 132 | 2.6106 | 2.9062 | 2.9208 | 2.6065 | 2.027 | 1.3757 | 0.60456 | -0.39159 | -1.2761 | -1.8465 | -2.0009 | -1.8915 | -1.7176 | -1.5705 | -1.527 | -1.4773 | -1.4909 | -1.4851 | -1.4209 | -1.4089 | -1.482 | -1.6739 | -1.8499 | -1.7786 | -1.5437 | -1.4043 | -1.3159 | -1.2756 | -1.2566 | -1.2251 | -1.1456 | -1.0458 | -0.88354 | -0.6975 | -0.61157 | -0.39492 | -0.33375 | -0.32927 | -0.38057 | -0.51473 | -0.55631 | -0.59496 | -0.61701 | -0.62478 | -0.561 | -0.42255 | -0.26017 | -0.079813 | 0.099341 | 0.29267 | 0.45621 | 0.62886 | 0.74913 | 0.86435 | 0.97908 | 1.0925 | 1.1228 | 1.0345 | 1.0351 | 1.2307 | 1.3938 | 1.496 | 1.5489 | 1.5294 | 1.4575 | 1.3438 | 1.2312 | 1.1019 | 0.90121 | 0.61818 | 0.26538 | -0.091108 | -0.74231 | -0.84449 | -1.1289 | -1.1497 | -0.8521 | -0.41687 | -0.0055736 | 0.37831 | 0.71669 | 1.0119 | 1.2373 | 1.4382 | 1.65 | 1.7978 | 1.7882 | 1.6773 | 1.507 | 1.3236 | 1.2536 | 1.3035 | 1.3619 | 0.70903 | 1.2522 | 1.2772 | 1.4535 | 1.7156 | 2.0914 | 2.4033 | 2.6314 | 2.7711 | 2.8522 | 2.9303 | 2.9561 | 3.085 | 3.2408 | 3.4649 | 3.7264 | 3.9731 | 4.0708 | 4.058 | 3.9683 | 3.5912 | 3.3299 | 3.0376 | 2.7385 | 2.4298 | 2.1689 | 1.8788 | 1.6625 | 0.85925 | -1.3212 | 1.1027 | 1.1519 | 1.2967 | 1.5246 | 1.7973 | 2.0125 | 1.4279 | 2.6429 | 2.8081 | 2.8572 | 2.8076 | 2.6695 | 2.4674 | 2.3192 | 2.1626 | 1.9913 | 1.8465 | 1.6923 | 1.5303 | 1.3486 | 1.256 | 1.284 | 1.4393 | 1.6652 | 1.8208 | 1.8796 | 2.0522 | 2.1612 | 2.1449 | 1.5036 | 1.9843 | 1.8819 | 1.7827 | 1.6546 | 1.4917 | 1.369 | 1.2859 | 1.2364 | 1.2511 | 1.4646 | 1.8149 | 2.1861 | 2.4491 | 2.5681 | 2.5938 | 2.461 | 2.237 | 1.9268 | 1.6166 | 1.3205 | 1.0571 | 0.93108 | 0.80154 | 0.69985 | 0.61893 | 0.54175 | 0.51487 | 0.55556 | 0.7419 | 0.85017 | 0.91205 | 0.93683 | 0.92684 | 0.82346 | 0.64963 | 0.49721 | 0.41892 | 0.33839 | 0.26176 | 0.17588 | 0.098237 | 0.0082677 | -0.059588 | -0.046264 | 0.023247 | 0.18535 | 0.31146 | 0.39154 | 0.38521 | 0.25899 | 0.049935 | -0.29494 | -0.57192 | -0.81858 | -0.99369 | -1.1253 | -1.277 | -1.4523 | -1.4238 | -1.4376 | -1.4861 | -1.4863 | -1.2846 | -1.0226 | -0.70344 | -0.43209 | -0.28697 | -0.22734 | -0.21621 | -0.18561 | -0.3194 | -0.51467 | -0.75987 | -1.0237 | -1.2598 | -1.3673 | -1.1665 | -0.53005 | 0.41335 | 1.2768 | 1.8079
|  | 156 | 2.9028 | 3.2255 | 3.2184 | 2.8826 | 2.3289 | 1.697 | 1.0094 | 0.15981 | -0.71529 | -1.3793 | -1.6815 | -1.7667 | -1.704 | -1.555 | -1.4229 | -1.2672 | -1.2395 | -1.2849 | -1.366 | -1.4989 | -1.7062 | -2.0047 | -1.9916 | -1.7877 | -1.6011 | -1.4331 | -1.2933 | -1.2174 | -1.1702 | -1.1329 | -1.0262 | -0.91768 | -0.74523 | -0.55278 | -0.47091 | -0.19636 | -0.19855 | -0.2258 | -0.3099 | -0.53907 | -0.58485 | -0.54113 | -0.57247 | -0.5762 | -0.49767 | -0.33675 | -0.1717 | 0.0058533 | 0.1932 | 0.38518 | 0.53688 | 0.70292 | 0.78833 | 0.85253 | 0.92476 | 1.0313 | 1.0598 | 0.94897 | 0.88516 | 1.0991 | 1.2691 | 1.3702 | 1.5176 | 1.5687 | 1.554 | 1.5015 | 1.4031 | 1.2658 | 1.0268 | 0.74232 | 0.35306 | -0.067259 | -0.84167 | -1.0271 | -1.4099 | -1.4766 | -1.2296 | -0.78898 | -0.36638 | 0.076373 | 0.52383 | 0.95086 | 1.277 | 1.4785 | 1.6946 | 1.8145 | 1.885 | 1.8182 | 1.6614 | 1.4248 | 1.2012 | 1.1169 | 1.0538 | 0.19781 | 0.74844 | 0.83734 | 1.1966 | 1.5836 | 2.0662 | 2.4378 | 2.7181 | 2.9223 | 3.0746 | 3.184 | 3.1919 | 3.2857 | 3.3348 | 3.3675 | 3.3881 | 3.4435 | 3.4459 | 3.4151 | 3.3623 | 3.0295 | 2.8795 | 2.7313 | 2.5431 | 2.3229 | 2.1053 | 1.8119 | 1.0654 | -1.3995 | 1.1407 | 1.0883 | 1.0241 | 1.0503 | 1.1197 | 1.2844 | 1.4357 | 0.94215 | 2.1515 | 2.4007 | 2.5868 | 2.6826 | 2.6717 | 2.5558 | 2.4282 | 2.2414 | 2.0409 | 1.8406 | 1.6337 | 1.4485 | 1.2222 | 1.0717 | 0.96135 | 0.96935 | 1.1342 | 1.1964 | 1.2488 | 1.5812 | 1.8947 | 2.0358 | 1.594 | 2.0992 | 1.9878 | 1.8631 | 1.7106 | 1.5804 | 1.4653 | 1.3566 | 1.3221 | 1.3347 | 1.4329 | 1.6121 | 1.9717 | 2.2959 | 2.4774 | 2.5368 | 2.4355 | 2.2631 | 1.9996 | 1.6966 | 1.3951 | 1.1123 | 0.96986 | 0.81187 | 0.68172 | 0.56577 | 0.42913 | 0.35575 | 0.27923 | 0.29411 | 0.24137 | 0.24341 | 0.29849 | 0.48086 | 0.66637 | 0.73507 | 0.73694 | 0.82365 | 0.62636 | 0.5029 | 0.36502 | 0.22588 | 0.12558 | 0.053547 | 0.053797 | 0.048376 | 0.054844 | 0.040395 | 0.082503 | 0.11211 | 0.055129 | -0.027746 | -0.27878 | -0.46455 | -0.65873 | -0.80401 | -0.89332 | -1.0257 | -1.1852 | -1.1669 | -1.1977 | -1.2246 | -1.2441 | -1.1538 | -1.0312 | -0.85111 | -0.62492 | -0.47638 | -0.41268 | -0.39186 | -0.25623 | -0.29676 | -0.43882 | -0.63634 | -0.8681 | -1.0642 | -1.1138 | -0.75741 | 0.14955 | 1.3518 | 2.2148 | 2.4056
|  | 180 | 2.7596 | 3.0752 | 3.0374 | 2.7717 | 2.2673 | 1.7315 | 1.1201 | 0.36601 | -0.44194 | -1.1128 | -1.5403 | -1.7497 | -1.7555 | -1.5897 | -1.395 | -1.2016 | -1.1669 | -1.295 | -1.4876 | -1.7306 | -1.9772 | -2.2112 | -2.0632 | -1.8245 | -1.6596 | -1.4967 | -1.3411 | -1.2408 | -1.1852 | -1.1398 | -1.0416 | -0.92617 | -0.74247 | -0.54002 | -0.43576 | -0.15392 | -0.17122 | -0.24307 | -0.35511 | -0.6332 | -0.75025 | -0.72627 | -0.72755 | -0.66721 | -0.55808 | -0.36591 | -0.19951 | -0.023907 | 0.16214 | 0.35064 | 0.49583 | 0.653 | 0.7195 | 0.72797 | 0.74225 | 0.7923 | 0.7826 | 0.7004 | 0.69269 | 0.89795 | 1.0675 | 1.2095 | 1.4377 | 1.5538 | 1.5896 | 1.5891 | 1.5148 | 1.3825 | 1.1203 | 0.81291 | 0.38024 | -0.099602 | -0.98052 | -1.2487 | -1.7208 | -1.8586 | -1.6532 | -1.2646 | -0.8264 | -0.31377 | 0.21307 | 0.70237 | 1.0862 | 1.3536 | 1.596 | 1.7673 | 1.8906 | 1.8838 | 1.7431 | 1.4709 | 1.1325 | 0.89425 | 0.69369 | -0.27412 | 0.33978 | 0.50111 | 0.92812 | 1.3962 | 1.9801 | 2.4295 | 2.7554 | 3.0312 | 3.2401 | 3.3878 | 3.3861 | 3.4395 | 3.3896 | 3.268 | 3.1109 | 2.9518 | 2.8123 | 2.725 | 2.6694 | 2.512 | 2.4887 | 2.4647 | 2.3914 | 2.2371 | 2.037 | 1.2527 | -1.4413 | 1.2175 | 1.1485 | 1.0258 | 0.92115 | 0.84342 | 0.78436 | 0.81765 | 0.89228 | 0.45495 | 1.5888 | 1.9613 | 2.2898 | 2.5363 | 2.6586 | 2.6231 | 2.5014 | 2.2965 | 2.0478 | 1.7989 | 1.5521 | 1.3448 | 1.1002 | 0.90017 | 0.69102 | 0.54687 | 0.58868 | 0.5787 | 0.68594 | 1.1174 | 1.5906 | 1.8856 | 1.6738 | 2.1569 | 2.0446 | 1.9013 | 1.7312 | 1.6013 | 1.4795 | 1.3786 | 1.3222 | 1.2972 | 1.2978 | 1.3515 | 1.6261 | 1.9229 | 2.1733 | 2.3108 | 2.2776 | 2.1762 | 1.9801 | 1.7183 | 1.4155 | 1.1275 | 0.96928 | 0.79423 | 0.62306 | 0.48809 | 0.31404 | 0.18159 | 0.02137 | -0.11548 | -0.30278 | -0.40321 | -0.28631 | 0.052478 | 0.47478 | 0.76729 | 0.94617 | 0.97317 | 0.85577 | 0.65378 | 0.45871 | 0.26349 | 0.14382 | 0.062774 | 0.026961 | -0.042184 | -0.14423 | -0.29483 | -0.37164 | -0.38006 | -0.39844 | -0.33681 | -0.4017 | -0.48662 | -0.59054 | -0.69272 | -0.76411 | -0.883 | -0.99114 | -0.94807 | -0.96497 | -0.97464 | -1.0507 | -1.09 | -1.1274 | -1.0816 | -0.94505 | -0.78662 | -0.64412 | -0.55674 | -0.42742 | -0.4539 | -0.54792 | -0.67549 | -0.83215 | -0.94496 | -0.90012 | -0.45237 | 0.47309 | 1.6647 | 2.4744 | 2.5388
|  | 204 | 2.4841 | 2.7225 | 2.6876 | 2.5039 | 2.1548 | 1.8177 | 1.3038 | 0.64897 | -0.074197 | -0.75568 | -1.3135 | -1.6494 | -1.7196 | -1.5459 | -1.3224 | -1.1107 | -1.0695 | -1.2511 | -1.5437 | -1.8886 | -2.1468 | -2.2989 | -2.0507 | -1.7798 | -1.6265 | -1.4712 | -1.3092 | -1.1943 | -1.1303 | -1.071 | -0.98711 | -0.87227 | -0.67972 | -0.46988 | -0.39684 | -0.062925 | -0.083439 | -0.17956 | -0.33809 | -0.68308 | -0.86733 | -0.81956 | -0.7758 | -0.64523 | -0.48455 | -0.28435 | -0.11274 | 0.05779 | 0.24081 | 0.41935 | 0.57451 | 0.71093 | 0.77858 | 0.757 | 0.69459 | 0.63165 | 0.52791 | 0.43802 | 0.4699 | 0.71583 | 0.93933 | 1.1368 | 1.4312 | 1.6033 | 1.6765 | 1.7342 | 1.6825 | 1.5668 | 1.2831 | 0.93736 | 0.46435 | -0.066685 | -1.0525 | -1.3904 | -1.9576 | -2.2415 | -2.0995 | -1.7083 | -1.202 | -0.60742 | -0.011993 | 0.53785 | 0.96426 | 1.2772 | 1.581 | 1.8023 | 1.9736 | 1.9924 | 1.8775 | 1.5799 | 1.133 | 0.73459 | 0.3792 | -0.60575 | -0.01934 | 0.25358 | 0.7554 | 1.3354 | 1.9917 | 2.5162 | 2.8815 | 3.2339 | 3.4876 | 3.6449 | 3.6355 | 3.6296 | 3.5039 | 3.2502 | 2.9369 | 2.5556 | 2.2356 | 2.0247 | 1.998 | 2.0351 | 2.2074 | 2.3251 | 2.3679 | 2.2484 | 1.4887 | -1.1821 | 1.4326 | 1.3056 | 1.1241 | 1.1219 | 0.87817 | 0.70657 | 0.54446 | 0.42452 | 0.37546 | -0.21917 | 1.0116 | 1.5493 | 2.0723 | 2.4968 | 2.7339 | 2.7485 | 2.6109 | 2.3814 | 2.0944 | 1.8076 | 1.5281 | 1.294 | 1.0421 | 0.7979 | 0.51391 | 0.22641 | 0.11469 | 0.064469 | 0.090704 | 0.663 | 1.3656 | 1.8387 | 1.69 | 2.3056 | 2.1789 | 2.0124 | 1.8257 | 1.691 | 1.5554 | 1.4623 | 1.4018 | 1.3336 | 1.2561 | 1.1898 | 1.3085 | 1.4849 | 1.8595 | 1.9453 | 2.0985 | 2.1276 | 2.0385 | 1.8455 | 1.5362 | 1.2501 | 1.076 | 0.87325 | 0.66141 | 0.50303 | 0.31278 | 0.11882 | -0.12317 | -0.41162 | -0.71246 | -0.87018 | -0.67984 | -0.18192 | 0.466 | 0.95776 | 1.2731 | 1.3366 | 1.1607 | 0.88818 | 0.62169 | 0.35137 | 0.20846 | 0.13365 | 0.068143 | -0.052904 | -0.25777 | -0.52055 | -0.73834 | -0.85244 | -0.88783 | -0.75569 | -0.5576 | -0.47294 | -0.44455 | -0.48024 | -0.54536 | -0.68001 | -0.77062 | -0.64746 | -0.65305 | -0.66376 | -0.81326 | -0.94882 | -1.1085 | -1.1969 | -1.168 | -1.0474 | -0.84745 | -0.68276 | -0.51921 | -0.50327 | -0.54412 | -0.5927 | -0.65432 | -0.66667 | -0.51759 | -0.035655 | 0.78144 | 1.7829 | 2.4391 | 2.4608
|  | 228 | 1.7939 | 1.9581 | 1.997 | 2.0112 | 2.019 | 1.9287 | 1.5391 | 0.99747 | 0.34907 | -0.35173 | -1.0378 | -1.5068 | -1.6434 | -1.4843 | -1.2665 | -1.0676 | -1.0389 | -1.2283 | -1.599 | -2.0816 | -2.519 | -2.8037 | -2.4434 | -1.9738 | -1.6883 | -1.4793 | -1.2879 | -1.1501 | -1.0872 | -1.0453 | -0.9825 | -0.88762 | -0.72715 | -0.51256 | -0.49124 | -0.050005 | 0.016294 | -0.12681 | -0.4325 | -0.88918 | -1.0976 | -0.93828 | -0.75907 | -0.53926 | -0.34052 | -0.1537 | 0.038449 | 0.19396 | 0.36272 | 0.52685 | 0.67824 | 0.7929 | 0.86828 | 0.83352 | 0.68863 | 0.46673 | 0.25121 | 0.13731 | 0.24243 | 0.52225 | 0.82214 | 1.1122 | 1.4166 | 1.6049 | 1.7079 | 1.8136 | 1.7884 | 1.7106 | 1.447 | 1.057 | 0.52876 | -0.036296 | -1.1101 | -1.5007 | -2.135 | -2.4728 | -2.3636 | -2.0037 | -1.4419 | -0.7575 | -0.090414 | 0.49484 | 0.92034 | 1.2789 | 1.6406 | 1.9047 | 2.074 | 2.0829 | 1.9668 | 1.6713 | 1.1699 | 0.5946 | 0.066718 | -1.0007 | -0.44419 | -0.068508 | 0.59755 | 1.3347 | 2.0608 | 2.6373 | 3.041 | 3.5029 | 3.7781 | 3.9054 | 3.8624 | 3.7778 | 3.5987 | 3.2897 | 2.8403 | 2.2799 | 1.7813 | 1.4669 | 1.4951 | 1.6354 | 1.9707 | 2.2563 | 2.4336 | 1.7844 | -1.0152 | 1.5936 | 1.5009 | 1.2767 | 1.1114 | 1.0733 | 0.80145 | 0.58802 | 0.36354 | 0.098989 | -0.05797 | -0.68278 | 0.48301 | 1.1567 | 1.893 | 2.5211 | 2.8296 | 2.8537 | 2.6659 | 2.4252 | 2.1093 | 1.7896 | 1.5011 | 1.2311 | 0.96007 | 0.68506 | 0.34208 | -0.041469 | -0.31527 | -0.48749 | -0.39015 | 0.2703 | 1.1308 | 1.7795 | 1.9715 | 2.4882 | 2.332 | 2.1081 | 1.9043 | 1.7372 | 1.5948 | 1.4737 | 1.3908 | 1.3115 | 1.1908 | 1.0481 | 0.95094 | 0.93296 | 1.1612 | 1.4504 | 1.773 | 1.9803 | 2.0498 | 1.9547 | 1.6742 | 1.3596 | 1.1258 | 0.88642 | 0.65472 | 0.48887 | 0.28459 | 0.033678 | -0.27846 | -0.66556 | -1.0362 | -1.2364 | -0.96194 | -0.29112 | 0.4895 | 1.1834 | 1.6458 | 1.7134 | 1.4913 | 1.1211 | 0.70862 | 0.3483 | 0.20191 | 0.16169 | 0.072561 | -0.088253 | -0.35997 | -0.70173 | -1.0678 | -1.3401 | -1.4876 | -1.317 | -0.88105 | -0.56348 | -0.33193 | -0.23504 | -0.26919 | -0.40908 | -0.45096 | -0.40368 | -0.40482 | -0.40381 | -0.60863 | -0.824 | -1.0424 | -1.2052 | -1.3049 | -1.3345 | -1.19 | -0.92074 | -0.71138 | -0.59526 | -0.53387 | -0.50118 | -0.45291 | -0.32024 | -0.090622 | 0.41943 | 1.1425 | 1.8415 | 2.1768 | 2.1189
|  | 252 | 1.2792 | 1.3641 | 1.4433 | 1.4842 | 1.5064 | 1.5426 | 1.3797 | 1.0262 | 0.47393 | -0.20005 | -0.86049 | -1.2456 | -1.3695 | -1.2092 | -1.0224 | -0.85312 | -0.86945 | -1.0221 | -1.3441 | -1.7949 | -2.2736 | -2.5703 | -2.4843 | -2.2152 | -1.8817 | -1.624 | -1.3844 | -1.2317 | -1.1056 | -0.9385 | -0.82198 | -0.70106 | -0.56387 | -0.32623 | -0.36473 | 0.018208 | 0.028169 | -0.17372 | -0.47442 | -0.818 | -0.92955 | -0.8634 | -0.67412 | -0.56418 | -0.51233 | -0.49342 | -0.15919 | 0.26313 | 0.59211 | 0.82991 | 0.97072 | 1.0673 | 1.0703 | 1.0285 | 0.87946 | 0.61076 | 0.3825 | 0.31467 | 0.40208 | 0.56806 | 0.82406 | 1.1703 | 1.486 | 1.5825 | 1.6236 | 1.9385 | 1.9723 | 1.8432 | 1.5386 | 1.1461 | 0.62665 | 0.025733 | -1.0931 | -1.3952 | -1.9928 | -2.3251 | -2.2847 | -1.9802 | -1.4499 | -0.74624 | 0.0074366 | 0.63522 | 1.0566 | 1.5147 | 1.8498 | 2.1391 | 2.2581 | 2.1968 | 2.0554 | 1.7503 | 1.2194 | 0.61316 | 0.0505 | -0.9888 | -0.36427 | -0.083633 | 0.46161 | 1.1139 | 1.7409 | 2.2311 | 2.6033 | 3.2515 | 3.6399 | 3.8263 | 3.8228 | 3.7344 | 3.5179 | 3.1771 | 2.7413 | 2.3146 | 1.9075 | 1.6141 | 1.5644 | 1.6833 | 1.8739 | 1.9751 | 1.4144 | -1.2953 | 1.1008 | 1.2754 | 1.2772 | 1.2463 | 1.1672 | 1.0353 | 0.84743 | 0.59211 | 0.36214 | 0.12815 | 0.013145 | -0.74672 | 0.30226 | 0.74911 | 1.2061 | 1.6968 | 2.0106 | 2.1842 | 2.2187 | 2.1677 | 1.9963 | 1.7197 | 1.4895 | 1.2456 | 0.93966 | 0.58671 | 0.19745 | -0.12013 | -0.39011 | -0.50271 | -0.36487 | 0.11992 | 0.74529 | 1.2763 | 1.4749 | 2.0124 | 2.0628 | 2.0804 | 2.0867 | 1.9548 | 1.8332 | 1.7163 | 1.5836 | 1.4478 | 1.2687 | 1.1115 | 0.96971 | 0.93817 | 1.0737 | 1.3671 | 1.6133 | 1.7404 | 1.7404 | 1.5779 | 1.3195 | 1.0513 | 0.90027 | 0.72947 | 0.56035 | 0.44436 | 0.23891 | -0.027575 | -0.31997 | -0.665 | -0.95341 | -1.1198 | -0.93691 | -0.43714 | 0.17154 | 0.72867 | 1.1362 | 1.2845 | 1.2115 | 1.1415 | 0.92096 | 0.64992 | 0.52208 | 0.42616 | 0.26997 | 0.038345 | -0.2665 | -0.60936 | -0.97654 | -1.2715 | -1.4443 | -1.348 | -1.0322 | -0.72625 | -0.4557 | -0.29359 | -0.28126 | -0.4398 | -0.40577 | -0.32467 | -0.25187 | -0.20612 | -0.32959 | -0.54288 | -0.76228 | -0.98076 | -1.1132 | -1.1293 | -1.0073 | -0.79132 | -0.66831 | -0.58854 | -0.51909 | -0.50406 | -0.38215 | -0.0672 | 0.33324 | 0.95315 | 1.592 | 1.9979 | 2.017 | 1.8082
|  | 276 | 1.0652 | 1.0692 | 1.0962 | 1.1164 | 1.127 | 1.094 | 0.96424 | 0.6614 | 0.1801 | -0.32556 | -0.77955 | -1.0507 | -1.1311 | -1.0218 | -0.92257 | -0.82364 | -0.86329 | -1.0029 | -1.2459 | -1.598 | -2.021 | -2.3449 | -2.4717 | -2.4708 | -2.3261 | -2.1541 | -1.911 | -1.6317 | -1.3409 | -1.0302 | -0.80261 | -0.59222 | -0.40042 | -0.21241 | -0.35138 | -0.018563 | -0.037875 | -0.19374 | -0.37281 | -0.55809 | -0.62027 | -0.6264 | -0.58406 | -0.61049 | -0.64728 | -0.63523 | -0.17774 | 0.41985 | 0.88492 | 1.1619 | 1.2826 | 1.324 | 1.2822 | 1.1919 | 1.0674 | 0.79958 | 0.57098 | 0.50548 | 0.50903 | 0.57935 | 0.76083 | 1.082 | 1.3714 | 1.4634 | 1.6097 | 2.0176 | 2.0508 | 1.8799 | 1.5431 | 1.159 | 0.22019 | 0.03084 | -1.4877 | -1.3639 | -1.8845 | -2.2262 | -2.2478 | -2.0167 | -1.6022 | -0.94982 | -0.16241 | 0.5609 | 1.0765 | 1.5888 | 1.927 | 2.2251 | 2.3429 | 2.2008 | 2.0211 | 1.714 | 1.1611 | 0.54961 | 0.10225 | -0.74751 | -0.30253 | -0.13568 | 0.21454 | 0.70656 | 1.2132 | 1.6846 | 2.1699 | 2.9077 | 3.3725 | 3.6189 | 3.6685 | 3.5935 | 3.3702 | 3.0133 | 2.597 | 2.234 | 1.9155 | 1.6582 | 1.5438 | 1.5522 | 1.5664 | 0.92421 | -1.7517 | 0.81809 | 0.65401 | 0.76992 | 0.98397 | 1.1237 | 1.1479 | 1.0192 | 0.80388 | 0.53556 | 0.32 | 0.16787 | 0.07377 | -0.74262 | 0.17429 | 0.38415 | 0.60593 | 0.92498 | 1.2321 | 1.5289 | 1.7829 | 1.908 | 1.8187 | 1.6268 | 1.4401 | 1.1994 | 0.84925 | 0.43838 | 0.028633 | -0.25221 | -0.43798 | -0.46634 | -0.34344 | -0.016982 | 0.38895 | 0.76395 | 0.84289 | 1.4892 | 1.7392 | 1.9132 | 2.0608 | 2.0636 | 1.9814 | 1.8474 | 1.6439 | 1.4373 | 1.2221 | 1.0725 | 0.98673 | 1.0069 | 1.1268 | 1.2971 | 1.4187 | 1.3865 | 1.2368 | 1.0047 | 0.7543 | 0.55926 | 0.47867 | 0.44365 | 0.36351 | 0.26551 | 0.058452 | -0.21908 | -0.47477 | -0.71852 | -0.87791 | -0.97757 | -0.88334 | -0.59264 | -0.22874 | 0.12079 | 0.37258 | 0.55946 | 0.7672 | 0.992 | 0.99569 | 0.92061 | 0.85366 | 0.67292 | 0.39412 | 0.052201 | -0.28032 | -0.5984 | -0.8971 | -1.1432 | -1.3251 | -1.3326 | -1.2087 | -1.077 | -0.92481 | -0.81352 | -0.7719 | -0.83815 | -0.79169 | -0.49354 | -0.27602 | -0.1055 | -0.17394 | -0.37303 | -0.56078 | -0.79005 | -0.89363 | -0.89451 | -0.82365 | -0.7022 | -0.65338 | -0.69776 | -0.67722 | -0.67828 | -0.46236 | 0.05982 | 0.70017 | 1.4087 | 1.9877 | 2.2345 | 2.0768 | 1.7268
|  | 300 | 0.99778 | 0.93274 | 0.92294 | 0.9341 | 0.98336 | 0.91182 | 0.71294 | 0.37742 | -0.037059 | -0.35882 | -0.58713 | -0.75513 | -0.83338 | -0.80512 | -0.81122 | -0.8215 | -0.89843 | -1.0126 | -1.169 | -1.4103 | -1.7681 | -2.0977 | -2.3895 | -2.6128 | -2.7019 | -2.6741 | -2.4699 | -2.0872 | -1.6004 | -1.1009 | -0.70722 | -0.38702 | -0.16657 | -0.051225 | -0.30218 | -0.029468 | -0.044807 | -0.11585 | -0.15401 | -0.20887 | -0.23641 | -0.29816 | -0.37653 | -0.4855 | -0.47818 | -0.24 | 0.31055 | 0.87864 | 1.3189 | 1.5655 | 1.6284 | 1.5734 | 1.4936 | 1.3835 | 1.2748 | 1.0231 | 0.78692 | 0.70651 | 0.623 | 0.59496 | 0.70716 | 1.001 | 1.278 | 1.4143 | 1.6653 | 2.0712 | 2.1189 | 1.961 | 1.6227 | 1.2105 | 0.6795 | 0.026081 | -1.0685 | -1.2497 | -1.7463 | -2.0611 | -2.1292 | -1.9921 | -1.714 | -1.1305 | -0.33801 | 0.49153 | 1.1465 | 1.6983 | 2.0564 | 2.3691 | 2.4706 | 2.2763 | 2.0511 | 1.7122 | 1.1422 | 0.55894 | 0.17988 | -0.63634 | -0.18678 | -0.10771 | 0.053292 | 0.35546 | 0.73221 | 1.18 | 1.715 | 2.5435 | 3.1002 | 3.423 | 3.537 | 3.4716 | 3.263 | 2.8923 | 2.5061 | 2.1923 | 1.9438 | 1.7532 | 1.6074 | 1.4913 | 0.69264 | -2.0555 | 0.4752 | 0.30184 | 0.15192 | 0.43721 | 0.8258 | 1.1023 | 1.1968 | 1.0567 | 0.79591 | 0.53146 | 0.33696 | 0.25925 | 0.16439 | -0.79707 | 0.14688 | 0.15285 | 0.16756 | 0.33002 | 0.61373 | 0.97808 | 1.419 | 1.6872 | 1.6922 | 1.5919 | 1.4374 | 1.188 | 0.78365 | 0.30898 | -0.11397 | -0.36831 | -0.45572 | -0.41128 | -0.29091 | -0.084409 | 0.135 | 0.35645 | 0.40051 | 1.0419 | 1.3928 | 1.7693 | 2.0953 | 2.2439 | 2.2101 | 2.0494 | 1.7522 | 1.4653 | 1.2249 | 1.0905 | 1.0723 | 1.1312 | 1.2526 | 1.3313 | 1.3258 | 1.1456 | 0.84755 | 0.51437 | 0.19698 | 0.10758 | 0.19307 | 0.26889 | 0.28801 | 0.19885 | -0.025939 | -0.3303 | -0.54002 | -0.68524 | -0.71497 | -0.73576 | -0.68945 | -0.54661 | -0.4233 | -0.27757 | -0.15245 | 0.077098 | 0.49288 | 0.96295 | 1.2078 | 1.3314 | 1.304 | 1.0495 | 0.60309 | 0.11501 | -0.26327 | -0.54449 | -0.75697 | -0.94204 | -1.1197 | -1.2331 | -1.2726 | -1.3159 | -1.2964 | -1.2474 | -1.1782 | -1.1563 | -0.99152 | -0.53911 | -0.16296 | 0.12153 | 0.063278 | -0.11834 | -0.30559 | -0.51486 | -0.60876 | -0.60596 | -0.5612 | -0.5256 | -0.56456 | -0.70411 | -0.74055 | -0.6936 | -0.33651 | 0.37293 | 1.2067 | 1.9717 | 2.4995 | 2.6613 | 2.3973 | 1.9229
|  | 324 | 1.0091 | 0.8808 | 0.83551 | 0.83346 | 0.87598 | 0.78017 | 0.55243 | 0.2153 | -0.15106 | -0.34639 | -0.38081 | -0.41277 | -0.45128 | -0.48643 | -0.6137 | -0.76258 | -0.88226 | -0.977 | -1.0464 | -1.1997 | -1.5015 | -1.8493 | -2.2674 | -2.6648 | -2.9679 | -3.1065 | -2.9661 | -2.4864 | -1.7267 | -1.0386 | -0.44405 | 0.0021617 | 0.20997 | 0.22313 | -0.19996 | 0.021868 | 0.037114 | 0.030351 | 0.1453 | 0.19106 | 0.1597 | 0.043536 | -0.12513 | -0.27426 | -0.22674 | 0.1269 | 0.78835 | 1.4668 | 1.9948 | 2.1994 | 2.1349 | 1.9239 | 1.7773 | 1.6339 | 1.5178 | 1.3058 | 1.0459 | 0.91775 | 0.75592 | 0.64133 | 0.6977 | 0.97109 | 1.2558 | 1.451 | 1.74 | 2.2028 | 2.3767 | 2.2642 | 1.8867 | 1.336 | 0.70613 | 0.048262 | -0.99074 | -1.1963 | -1.6043 | -1.8601 | -1.9604 | -1.9278 | -1.7917 | -1.2801 | -0.52613 | 0.33849 | 1.1918 | 1.8085 | 2.2113 | 2.5584 | 2.6329 | 2.3664 | 2.0862 | 1.6843 | 1.1155 | 0.6061 | 0.27562 | -0.42487 | -0.067842 | -0.066369 | -0.04316 | 0.0804 | 0.25398 | 0.58773 | 1.1754 | 2.1176 | 2.8515 | 3.3262 | 3.5098 | 3.4427 | 3.1882 | 2.802 | 2.4549 | 2.174 | 2.0225 | 1.9413 | 1.7793 | 0.9074 | -1.9366 | 0.3981 | 0.052797 | -0.10392 | -0.029875 | 0.35497 | 0.87717 | 1.2685 | 1.4405 | 1.2258 | 0.859 | 0.57055 | 0.39764 | 0.38213 | 0.34049 | -0.57897 | 0.1411 | -0.021577 | -0.18598 | -0.17801 | 0.037687 | 0.38215 | 0.95157 | 1.3945 | 1.5776 | 1.61 | 1.4927 | 1.2215 | 0.74591 | 0.21008 | -0.23114 | -0.45812 | -0.45521 | -0.3424 | -0.20624 | -0.11305 | -0.048103 | 0.028423 | 0.10842 | 0.71813 | 1.1762 | 1.7467 | 2.2838 | 2.583 | 2.5859 | 2.3786 | 1.9514 | 1.5331 | 1.2442 | 1.1182 | 1.179 | 1.283 | 1.4007 | 1.39 | 1.2618 | 0.95255 | 0.51502 | 0.053805 | -0.36011 | -0.32538 | -0.032266 | 0.1907 | 0.31759 | 0.24163 | -0.026372 | -0.37463 | -0.55284 | -0.62313 | -0.55529 | -0.48621 | -0.46108 | -0.45223 | -0.5322 | -0.57791 | -0.59106 | -0.35569 | 0.23051 | 1.0468 | 1.6326 | 1.9583 | 1.9636 | 1.624 | 0.94315 | 0.25595 | -0.21047 | -0.47249 | -0.59856 | -0.72099 | -0.89214 | -1.0996 | -1.2925 | -1.5045 | -1.6147 | -1.6396 | -1.6044 | -1.4874 | -1.024 | -0.42886 | 0.1574 | 0.56114 | 0.47057 | 0.25599 | 0.011311 | -0.19508 | -0.29213 | -0.28539 | -0.24189 | -0.29035 | -0.42515 | -0.64907 | -0.72752 | -0.62778 | -0.1322 | 0.72595 | 1.8615 | 2.7107 | 3.1654 | 3.2157 | 2.8022 | 2.1825
|  | 348 | 1.0694 | 0.8925 | 0.81073 | 0.8136 | 0.81747 | 0.72573 | 0.51954 | 0.23348 | -0.10176 | -0.26021 | -0.20423 | -0.085421 | -0.068395 | -0.15107 | -0.36435 | -0.57028 | -0.70653 | -0.75669 | -0.81325 | -0.93071 | -1.1763 | -1.5121 | -2.0097 | -2.5172 | -2.9661 | -3.2413 | -3.1521 | -2.6123 | -1.8047 | -0.9466 | -0.15308 | 0.4204 | 0.63225 | 0.56443 | 0.1109 | 0.37367 | 0.38328 | 0.45949 | 0.59483 | 0.6526 | 0.61792 | 0.4268 | 0.22717 | 0.12854 | 0.25235 | 0.64058 | 1.2534 | 2.0144 | 2.656 | 2.8671 | 2.7354 | 2.4464 | 2.209 | 2.1731 | 1.9983 | 1.7359 | 1.4241 | 1.1824 | 0.95094 | 0.82513 | 0.80327 | 0.93489 | 1.2351 | 1.4737 | 1.8031 | 2.2129 | 2.5022 | 2.4393 | 2.0314 | 1.4692 | 0.78321 | 0.11371 | -0.88319 | -1.0315 | -1.4042 | -1.5876 | -1.7383 | -1.7868 | -1.6676 | -1.2257 | -0.50131 | 0.37025 | 1.1232 | 1.7092 | 2.1988 | 2.5218 | 2.6694 | 2.6024 | 2.2549 | 1.7618 | 1.27 | 0.90134 | 0.61451 | -0.19306 | 0.17158 | 0.084165 | 0.047275 | 0.082791 | 0.14609 | 0.40128 | 0.93801 | 1.7707 | 2.4833 | 3.024 | 3.2717 | 3.3244 | 3.1433 | 2.8072 | 2.529 | 2.3053 | 2.1685 | 2.0803 | 1.4615 | -1.4526 | 0.81535 | 0.38639 | -0.0012557 | -0.044327 | 0.086143 | 0.42098 | 0.82815 | 1.1921 | 1.3778 | 1.2005 | 0.79684 | 0.55119 | 0.47715 | 0.50746 | 0.4871 | -0.47806 | 0.16542 | -0.081316 | -0.31155 | -0.36531 | -0.19595 | 0.15228 | 0.67623 | 1.1108 | 1.3301 | 1.4038 | 1.3321 | 1.0612 | 0.57807 | 0.043081 | -0.32075 | -0.53212 | -0.49103 | -0.34754 | -0.25056 | -0.17793 | -0.17018 | -0.059256 | -0.068308 | 0.63405 | 1.1992 | 1.7783 | 2.3436 | 2.7077 | 2.7667 | 2.5393 | 2.1157 | 1.6888 | 1.4359 | 1.3496 | 1.4469 | 1.5766 | 1.6314 | 1.5663 | 1.3551 | 0.99135 | 0.49023 | -0.070325 | -0.44932 | -0.44765 | -0.15999 | 0.1457 | 0.34758 | 0.33156 | 0.12944 | -0.20951 | -0.39108 | -0.41431 | -0.30994 | -0.21435 | -0.19435 | -0.29363 | -0.49219 | -0.65579 | -0.69436 | -0.45911 | 0.19157 | 1.1429 | 1.9801 | 2.4975 | 2.5013 | 2.125 | 1.2614 | 0.47532 | 0.067087 | -0.22491 | -0.29364 | -0.38119 | -0.56941 | -0.876 | -1.2168 | -1.5463 | -1.7731 | -1.8753 | -1.8488 | -1.6517 | -1.0846 | -0.24403 | 0.53369 | 1.0343 | 0.99103 | 0.64519 | 0.38094 | 0.18699 | 0.096769 | 0.12663 | 0.13409 | 0.018982 | -0.19229 | -0.44031 | -0.54946 | -0.41115 | 0.15377 | 1.0032 | 2.3085 | 3.2895 | 3.7125 | 3.6984 | 3.2354 | 2.4717
|  | 372 | 1.1232 | 0.91675 | 0.82407 | 0.79891 | 0.76512 | 0.71757 | 0.58058 | 0.40076 | 0.17588 | 0.034642 | -0.042467 | -0.19113 | -0.38301 | -0.54465 | -0.64931 | -0.57249 | -0.55337 | -0.5244 | -0.59321 | -0.73326 | -0.97482 | -1.3439 | -1.8619 | -2.4293 | -2.8391 | -3.0801 | -2.9932 | -2.6153 | -2.0287 | -1.3489 | -0.75743 | -0.26019 | 0.098478 | 0.45593 | 0.44167 | 0.95794 | 1.0142 | 1.0572 | 1.1219 | 1.0242 | 0.85623 | 0.56805 | 0.36869 | 0.33184 | 0.45273 | 0.68899 | 1.0758 | 1.6004 | 2.0293 | 2.2964 | 2.4063 | 2.3574 | 2.354 | 2.5286 | 2.3515 | 2.0267 | 1.6553 | 1.3591 | 1.0383 | 0.81955 | 0.72709 | 0.73912 | 0.93926 | 1.171 | 1.4828 | 1.6764 | 1.7181 | 1.6033 | 1.3151 | 1.063 | 0.69842 | 0.19145 | -0.67173 | -0.75945 | -1.1273 | -1.3722 | -1.6363 | -1.6773 | -1.5391 | -1.144 | -0.47397 | 0.24965 | 0.70893 | 1.0419 | 1.4115 | 1.7396 | 2.086 | 2.3278 | 2.1936 | 1.7821 | 1.3781 | 1.0541 | 0.76217 | -0.15709 | 0.098433 | -0.076541 | -0.13109 | -0.01812 | 0.17112 | 0.50307 | 0.96228 | 1.5008 | 1.8724 | 2.1437 | 2.3653 | 2.6619 | 2.8199 | 2.6996 | 2.5658 | 2.3761 | 2.1509 | 1.4006 | -1.4996 | 1.134 | 0.77368 | 0.39122 | 0.09242 | -0.014218 | -0.068238 | 0.040779 | 0.20781 | 0.30622 | 0.40841 | 0.43463 | 0.37046 | 0.33901 | 0.38803 | 0.44334 | 0.43279 | -0.54187 | 0.083058 | -0.17734 | -0.36461 | -0.4079 | -0.2563 | 0.071048 | 0.43776 | 0.73221 | 0.77725 | 0.74542 | 0.63333 | 0.43118 | 0.10129 | -0.25387 | -0.45284 | -0.59005 | -0.6091 | -0.55776 | -0.56807 | -0.44444 | -0.30564 | -0.0042224 | 0.13179 | 0.69995 | 1.1099 | 1.4565 | 1.7662 | 1.9042 | 1.9343 | 1.7613 | 1.6254 | 1.508 | 1.4834 | 1.5503 | 1.6232 | 1.679 | 1.6162 | 1.4956 | 1.2999 | 1.0043 | 0.56839 | 0.045253 | -0.32784 | -0.5028 | -0.48571 | -0.4191 | -0.32429 | -0.24507 | -0.15797 | -0.17952 | -0.26827 | -0.23221 | -0.12584 | -0.08922 | -0.15295 | -0.34509 | -0.50736 | -0.63069 | -0.58712 | -0.33632 | 0.095225 | 0.64913 | 1.2024 | 1.5849 | 1.5443 | 1.1817 | 0.64779 | 0.29283 | 0.1844 | 0.033071 | 0.039679 | -0.014521 | -0.27258 | -0.70254 | -1.171 | -1.5014 | -1.7029 | -1.7541 | -1.7013 | -1.5584 | -1.1005 | -0.46477 | 0.026756 | 0.33954 | 0.52137 | 0.56167 | 0.48526 | 0.49533 | 0.48322 | 0.52995 | 0.4708 | 0.295 | 0.022511 | -0.20297 | -0.30901 | -0.22228 | 0.13751 | 0.6715 | 1.683 | 2.6111 | 3.2618 | 3.5155 | 3.1623 | 2.4779
|  | 396 | 1.1852 | 0.96876 | 0.83014 | 0.75959 | 0.66854 | 0.64033 | 0.60077 | 0.53519 | 0.41194 | 0.2961 | 0.12616 | -0.1825 | -0.53733 | -0.86622 | -0.93181 | -0.72287 | -0.49449 | -0.38193 | -0.41805 | -0.58022 | -0.86817 | -1.2837 | -1.8146 | -2.3741 | -2.7365 | -2.9343 | -2.8639 | -2.5662 | -2.1553 | -1.6512 | -1.2207 | -0.76946 | -0.2851 | 0.39403 | 0.5792 | 1.3302 | 1.532 | 1.5309 | 1.4564 | 1.2412 | 0.95213 | 0.64633 | 0.44388 | 0.41643 | 0.5114 | 0.69157 | 0.98209 | 1.3466 | 1.6767 | 1.913 | 2.0858 | 2.2126 | 2.4169 | 2.6328 | 2.55 | 2.3036 | 1.9189 | 1.557 | 1.1519 | 0.81011 | 0.63399 | 0.59281 | 0.77317 | 0.98356 | 1.2409 | 1.3054 | 1.225 | 1.0555 | 0.82993 | 0.77268 | 0.67159 | 0.33981 | -0.34473 | -0.3994 | -0.80895 | -1.1746 | -1.4835 | -1.5118 | -1.3391 | -0.96392 | -0.46352 | 0.018621 | 0.29252 | 0.443 | 0.69665 | 1.0682 | 1.5354 | 1.9704 | 2.0915 | 1.8802 | 1.5581 | 1.2638 | 0.95788 | -0.36605 | 0.10756 | -0.16003 | -0.22304 | -0.039909 | 0.28405 | 0.67029 | 1.0489 | 1.3719 | 1.508 | 1.5058 | 1.5585 | 1.8815 | 2.3343 | 2.5368 | 2.6071 | 2.4927 | 1.6234 | -1.2505 | 1.4134 | 1.07 | 0.69552 | 0.4662 | 0.23856 | 0.056012 | -0.13062 | -0.2536 | -0.31134 | -0.38792 | -0.31509 | -0.13732 | 0.12459 | 0.36248 | 0.46903 | 0.53676 | 0.49161 | -0.5526 | 0.092679 | -0.17269 | -0.30291 | -0.36671 | -0.24672 | -0.01429 | 0.25446 | 0.44188 | 0.39373 | 0.32218 | 0.16906 | 0.042069 | -0.092044 | -0.26965 | -0.4387 | -0.53429 | -0.62217 | -0.70871 | -0.78836 | -0.67051 | -0.36571 | -0.017445 | 0.19548 | 0.88562 | 1.233 | 1.4543 | 1.5571 | 1.5185 | 1.4307 | 1.3269 | 1.4 | 1.5097 | 1.6885 | 1.8475 | 1.8837 | 1.8171 | 1.6193 | 1.4267 | 1.2133 | 0.99744 | 0.65134 | 0.23253 | -0.1352 | -0.47665 | -0.68039 | -0.82205 | -0.80604 | -0.71778 | -0.45185 | -0.15744 | -0.093975 | 0.0021842 | 0.10692 | 0.053363 | -0.10357 | -0.37989 | -0.54598 | -0.59375 | -0.49558 | -0.24159 | 0.081799 | 0.46689 | 0.79795 | 0.99395 | 0.85828 | 0.55011 | 0.28461 | 0.19774 | 0.22136 | 0.27277 | 0.36127 | 0.28707 | -0.053343 | -0.58108 | -1.1302 | -1.532 | -1.7518 | -1.7643 | -1.6121 | -1.4139 | -1.0417 | -0.63855 | -0.39306 | -0.19873 | 0.15319 | 0.48825 | 0.64665 | 0.87963 | 1.0045 | 1.0293 | 0.90587 | 0.61721 | 0.29941 | 0.071963 | -0.0010658 | 0.06355 | 0.2957 | 0.69802 | 1.3708 | 2.1025 | 2.6756 | 2.8819 | 2.6561 | 2.3229
|  | 420 | 1.3148 | 1.0799 | 0.91203 | 0.7839 | 0.64514 | 0.63519 | 0.68936 | 0.7527 | 0.74918 | 0.66814 | 0.42567 | -0.048168 | -0.57419 | -1.0491 | -1.1491 | -0.83935 | -0.37675 | -0.13972 | -0.11794 | -0.29967 | -0.65014 | -1.1597 | -1.71 | -2.2453 | -2.5577 | -2.7321 | -2.67 | -2.4199 | -2.1429 | -1.8092 | -1.5581 | -1.1274 | -0.47656 | 0.47391 | 0.32727 | 1.9112 | 2.2073 | 2.1766 | 1.9521 | 1.5646 | 1.1334 | 0.77799 | 0.59911 | 0.56972 | 0.63062 | 0.74282 | 0.9608 | 1.2211 | 1.4709 | 1.6734 | 1.8346 | 2.0222 | 2.4525 | 2.8389 | 2.891 | 2.7109 | 2.3077 | 1.8573 | 1.3244 | 0.8669 | 0.58927 | 0.52825 | 0.68219 | 0.89515 | 1.1033 | 1.0647 | 0.85653 | 0.59835 | 0.45193 | 0.56851 | 0.77086 | 0.68752 | 0.16591 | 0.11497 | -0.40622 | -0.93316 | -1.3252 | -1.3 | -1.0617 | -0.67743 | -0.3005 | -0.036796 | 0.028805 | -0.084054 | 0.047809 | 0.50302 | 1.1445 | 1.7419 | 2.1647 | 2.1842 | 1.9554 | 1.6323 | 1.2001 | 0.14228 | 0.19619 | -0.17589 | -0.2386 | 0.0026791 | 0.43873 | 0.8937 | 1.2397 | 1.4099 | 1.3186 | 1.0302 | 0.83468 | 1.0664 | 1.8018 | 2.4184 | 2.7454 | 2.0217 | -0.83263 | 1.914 | 1.4223 | 0.93806 | 0.66137 | 0.57395 | 0.43759 | 0.24252 | -0.081382 | -0.41309 | -0.7153 | -0.97363 | -0.94949 | -0.68913 | -0.20196 | 0.40788 | 0.67254 | 0.74507 | 0.6087 | -0.59566 | 0.14072 | -0.10447 | -0.20479 | -0.25593 | -0.19795 | -0.028024 | 0.1538 | 0.25168 | 0.14562 | 0.0055065 | -0.15958 | -0.31053 | -0.33696 | -0.28 | -0.33618 | -0.42913 | -0.59447 | -0.83475 | -0.98862 | -0.86031 | -0.39014 | 0.16932 | 0.57335 | 1.1879 | 1.4733 | 1.5765 | 1.4629 | 1.2666 | 1.0788 | 1.0527 | 1.3552 | 1.8064 | 2.1278 | 2.3101 | 2.2548 | 2.048 | 1.6985 | 1.3921 | 1.1903 | 1.0646 | 0.85024 | 0.49438 | 0.10613 | -0.36223 | -0.77787 | -1.112 | -1.2015 | -1.0766 | -0.68509 | -0.15526 | 0.15683 | 0.38238 | 0.4651 | 0.34048 | 0.033027 | -0.3454 | -0.5082 | -0.50759 | -0.36082 | -0.10969 | 0.18086 | 0.4541 | 0.64857 | 0.69562 | 0.45123 | 0.14918 | 0.028253 | 0.18042 | 0.46313 | 0.72309 | 0.83543 | 0.73811 | 0.29871 | -0.33822 | -0.97522 | -1.4782 | -1.7266 | -1.6762 | -1.4042 | -1.1754 | -1.3053 | -0.64015 | -0.60811 | -0.56753 | -0.13497 | 0.48913 | 0.98409 | 1.4279 | 1.6572 | 1.6496 | 1.4357 | 1.0131 | 0.63863 | 0.41082 | 0.36509 | 0.4191 | 0.56277 | 0.82901 | 1.2845 | 1.8717 | 2.3817 | 2.5864 | 2.4653 | 2.2872
|  | 444 | 1.5684 | 1.3633 | 1.1051 | 0.89133 | 0.71592 | 0.70364 | 0.87878 | 1.1498 | 1.384 | 1.3279 | 0.94454 | 0.24136 | -0.48091 | -1.0793 | -1.2497 | -0.8894 | -0.091301 | 0.40003 | 0.48051 | 0.2208 | -0.28657 | -0.9438 | -1.5624 | -2.0332 | -2.2853 | -2.4621 | -2.4311 | -2.2584 | -2.0802 | -1.8717 | -1.7656 | -1.3126 | -0.41117 | 0.79482 | 1.4954 | 2.9134 | 3.2209 | 3.0326 | 2.6026 | 2.0504 | 1.4771 | 1.0343 | 0.8186 | 0.78346 | 0.79403 | 0.87605 | 1.05 | 1.2245 | 1.3888 | 1.5557 | 1.6667 | 1.86 | 2.5365 | 3.2438 | 3.543 | 3.4057 | 2.9783 | 2.4295 | 1.6716 | 1.0336 | 0.68395 | 0.64083 | 0.79755 | 0.96853 | 1.087 | 1.0035 | 0.7124 | 0.43491 | 0.36592 | 0.64204 | 1.2505 | 1.6092 | 1.1685 | 1.1165 | 0.40632 | -0.35124 | -0.91255 | -0.85652 | -0.58632 | -0.1074 | 0.22211 | 0.21212 | -0.088829 | -0.44011 | -0.41898 | 0.21876 | 1.1217 | 1.824 | 2.5637 | 2.8555 | 2.6668 | 2.1976 | 1.4317 | 0.11087 | 0.29524 | -0.16621 | -0.18632 | 0.060636 | 0.54388 | 1.0807 | 1.4528 | 1.4717 | 1.1897 | 0.71192 | 0.32268 | 0.42068 | 1.3907 | 2.518 | 2.4187 | -0.21611 | 2.769 | 2.3181 | 1.6122 | 0.93822 | 0.72868 | 0.7493 | 0.78151 | 0.63731 | 0.11738 | -0.46665 | -0.9872 | -1.4099 | -1.4585 | -1.2073 | -0.57385 | 0.48876 | 1.0577 | 1.1888 | 0.94073 | -0.30459 | 0.29085 | 0.039828 | -0.045119 | -0.10591 | -0.12468 | -0.015343 | 0.089016 | 0.12659 | -0.0061805 | -0.2042 | -0.38726 | -0.57269 | -0.64949 | -0.25096 | 0.020044 | -0.011977 | -0.36485 | -0.70846 | -0.94754 | -0.76093 | -0.19768 | 0.52012 | 1.0825 | 1.7577 | 1.899 | 1.8387 | 1.5632 | 1.2319 | 0.95678 | 0.92572 | 1.3755 | 2.2961 | 2.8507 | 3.0582 | 2.863 | 2.4304 | 1.9568 | 1.5179 | 1.3081 | 1.2281 | 1.0975 | 0.7903 | 0.34241 | -0.21016 | -0.79162 | -1.2776 | -1.4816 | -1.3246 | -0.86141 | -0.059817 | 0.67385 | 1.0665 | 1.153 | 0.91262 | 0.431 | -0.11185 | -0.31119 | -0.30206 | -0.15129 | 0.097679 | 0.36461 | 0.5677 | 0.67376 | 0.5892 | 0.25461 | -0.14476 | -0.27937 | 0.20958 | 0.98603 | 1.5 | 1.4776 | 1.2207 | 0.64271 | -0.12313 | -0.84923 | -1.4847 | -1.7757 | -1.5867 | -1.0553 | -0.67343 | -0.60779 | -0.64093 | -0.77951 | -0.86228 | -0.40626 | 0.68066 | 1.6872 | 2.33 | 2.6345 | 2.5619 | 2.2783 | 1.5973 | 0.98857 | 0.72441 | 0.75415 | 0.81335 | 0.85828 | 0.99113 | 1.2805 | 1.7432 | 2.2263 | 2.5552 | 2.6033 | 2.4143
|  | 468 | 1.5244 | 1.3013 | 1.1136 | 0.97294 | 0.79274 | 0.83962 | 1.0374 | 1.2538 | 1.4647 | 1.3806 | 0.99203 | 0.41695 | -0.28085 | -0.82309 | -0.97818 | -0.71456 | -0.24326 | 0.19721 | 0.31172 | 0.075514 | -0.24675 | -0.81865 | -1.6103 | -1.8969 | -1.9612 | -2.0893 | -2.0745 | -1.9606 | -1.8226 | -1.6632 | -1.4637 | -0.88928 | 0.0057327 | 0.95732 | 1.4078 | 2.8879 | 3.2269 | 3.1121 | 2.817 | 2.4354 | 2.0138 | 1.5258 | 1.2917 | 1.2289 | 1.2897 | 1.3726 | 1.4109 | 1.5 | 1.6515 | 1.7588 | 1.8515 | 2.0539 | 2.3881 | 2.8933 | 3.2099 | 3.1301 | 2.7837 | 2.4146 | 2.0835 | 1.4421 | 0.96244 | 0.89611 | 1.0182 | 1.1573 | 1.1273 | 0.9844 | 0.78148 | 0.65086 | 0.61801 | 0.65564 | 0.89959 | 1.1844 | 0.87897 | 0.87289 | 0.38752 | -0.023912 | -0.55814 | -0.56769 | -0.47475 | -0.20453 | -0.016243 | -0.048255 | -0.33687 | -0.6341 | -0.65674 | -0.2228 | 0.45032 | 1.186 | 1.8652 | 2.2357 | 2.2041 | 1.8522 | 1.3079 | 0.07562 | 0.52965 | 0.17667 | 0.14121 | 0.35125 | 0.79582 | 1.2681 | 1.5191 | 1.5087 | 1.279 | 0.84817 | 0.38741 | 0.32763 | 0.87841 | 1.3215 | -0.69549 | 2.138 | 2.0018 | 1.7189 | 1.4472 | 1.0371 | 0.9486 | 0.85131 | 0.70564 | 0.44086 | -0.053117 | -0.58882 | -1.0787 | -1.4538 | -1.4857 | -1.3968 | -0.93298 | -0.28342 | 0.24449 | 0.48716 | 0.50396 | -0.37518 | 0.46361 | 0.2948 | 0.27673 | 0.26379 | 0.20271 | 0.21286 | 0.19745 | 0.10891 | -0.11906 | -0.33033 | -0.47836 | -0.53234 | -0.56524 | -0.45938 | -0.36757 | -0.45138 | -0.69923 | -0.95853 | -1.1492 | -0.88115 | -0.40353 | 0.25193 | 0.80422 | 1.382 | 1.6126 | 1.6373 | 1.5303 | 1.2327 | 0.97415 | 0.90135 | 1.2174 | 1.802 | 2.2752 | 2.4503 | 2.3507 | 2.1202 | 1.945 | 1.82 | 1.6651 | 1.5392 | 1.3292 | 0.98083 | 0.44503 | -0.2048 | -0.85166 | -1.3433 | -1.5537 | -1.393 | -0.96938 | -0.38709 | 0.27068 | 0.63319 | 0.73461 | 0.55268 | 0.18968 | -0.16505 | -0.21344 | -0.04626 | 0.12007 | 0.3553 | 0.60811 | 0.76801 | 0.7923 | 0.63318 | 0.33523 | -0.075802 | -0.21112 | 0.13801 | 0.80096 | 1.2499 | 1.2217 | 1.0578 | 0.64958 | -0.11561 | -0.78339 | -1.304 | -1.561 | -1.3211 | -0.95929 | -0.6771 | -0.71343 | -0.71262 | -0.85278 | -0.86 | -0.39819 | 0.52285 | 1.509 | 2.2054 | 2.537 | 2.4831 | 2.2336 | 1.8982 | 1.3292 | 1.1289 | 1.2294 | 1.2794 | 1.2583 | 1.2747 | 1.4286 | 1.7697 | 2.1517 | 2.3812 | 2.443 | 2.3053
|  | 492 | 1.2372 | 0.96793 | 0.83751 | 0.91566 | 0.81657 | 0.89287 | 1.0274 | 1.099 | 1.0888 | 0.94823 | 0.58831 | 0.22702 | -0.23441 | -0.5397 | -0.66015 | -0.65314 | -0.53248 | -0.49125 | -0.50421 | -0.69797 | -0.84243 | -1.1948 | -1.9132 | -2.0505 | -1.9815 | -2.0174 | -1.9602 | -1.8268 | -1.7237 | -1.5298 | -1.2395 | -0.64463 | 0.048913 | 0.75596 | 0.83049 | 2.0374 | 2.3958 | 2.4407 | 2.3719 | 2.2836 | 2.1653 | 1.8053 | 1.6594 | 1.58 | 1.5615 | 1.5928 | 1.5257 | 1.5746 | 1.7217 | 1.8233 | 1.8894 | 1.9757 | 2.1415 | 2.3221 | 2.4739 | 2.387 | 2.1918 | 2.1173 | 2.0269 | 1.524 | 1.1453 | 1.0281 | 1.0199 | 0.97802 | 0.8771 | 0.712 | 0.60763 | 0.59895 | 0.56381 | 0.51786 | 0.31893 | 0.64631 | -0.23807 | 0.33912 | 0.042104 | -0.22394 | -0.49382 | -0.54325 | -0.47085 | -0.28177 | -0.19341 | -0.24047 | -0.51064 | -0.76723 | -0.84553 | -0.62689 | -0.14721 | 0.51449 | 1.1719 | 1.5425 | 1.6251 | 1.4617 | 1.162 | 0.099049 | 0.80244 | 0.60825 | 0.56314 | 0.67774 | 1.0077 | 1.3573 | 1.5059 | 1.4544 | 1.2571 | 0.93092 | 0.52759 | 0.36684 | 0.11954 | -1.777 | 0.96793 | 1.2144 | 1.1579 | 1.1898 | 1.4047 | 1.2272 | 1.1969 | 1.011 | 0.71925 | 0.31087 | -0.28619 | -0.86546 | -1.2721 | -1.5379 | -1.5288 | -1.4703 | -1.1135 | -0.73563 | -0.43511 | -0.22774 | -0.048274 | -0.74211 | 0.46091 | 0.52124 | 0.61532 | 0.66393 | 0.53208 | 0.41179 | 0.22008 | -0.012666 | -0.32556 | -0.55491 | -0.60939 | -0.55263 | -0.53024 | -0.51271 | -0.5905 | -0.80024 | -1.0982 | -1.3104 | -1.3338 | -1.065 | -0.59806 | 0.0082014 | 0.43037 | 1.0097 | 1.2991 | 1.4306 | 1.4689 | 1.2922 | 1.0993 | 1.0084 | 1.135 | 1.4192 | 1.6093 | 1.7155 | 1.6988 | 1.7147 | 1.905 | 2.026 | 1.934 | 1.8009 | 1.4867 | 1.0527 | 0.38339 | -0.38146 | -1.0592 | -1.4975 | -1.6291 | -1.4538 | -1.1098 | -0.73418 | -0.36792 | -0.16998 | -0.12782 | -0.24997 | -0.42075 | -0.45806 | -0.26741 | 0.059438 | 0.3193 | 0.52042 | 0.73016 | 0.77401 | 0.71642 | 0.53989 | 0.30167 | 0.052549 | -0.094604 | 0.075333 | 0.36293 | 0.54673 | 0.45726 | 0.29062 | 0.12202 | -0.29095 | -0.73831 | -0.9033 | -1.0962 | -1.0037 | -0.92003 | -0.88246 | -0.97956 | -0.86433 | -0.80862 | -0.70947 | -0.31273 | 0.28008 | 0.97084 | 1.4933 | 1.8193 | 1.9148 | 1.9662 | 2.0208 | 1.717 | 1.699 | 1.7732 | 1.758 | 1.6061 | 1.4498 | 1.4491 | 1.6598 | 1.9467 | 2.0797 | 2.0716 | 2.0038
|  | 516 | 1.0929 | 0.77981 | 0.61087 | 0.84049 | 0.89185 | 1.0178 | 1.1465 | 1.1498 | 1.0048 | 0.72822 | 0.37255 | 0.15402 | -0.048795 | -0.12704 | -0.23589 | -0.39659 | -0.5292 | -0.78543 | -1.0257 | -1.3201 | -1.5134 | -1.7599 | -2.1452 | -2.1719 | -2.01 | -1.9251 | -1.8174 | -1.6823 | -1.6054 | -1.3413 | -0.98934 | -0.42296 | 0.14406 | 0.71443 | 0.6041 | 1.5762 | 1.8422 | 1.924 | 1.9878 | 2.0917 | 2.2654 | 2.1511 | 2.1199 | 2.032 | 1.9139 | 1.8155 | 1.6896 | 1.6956 | 1.8247 | 1.9575 | 1.99 | 2.0021 | 2.0168 | 1.9869 | 1.9788 | 1.9037 | 1.8388 | 1.9118 | 1.9501 | 1.6588 | 1.4317 | 1.2792 | 1.1347 | 0.84803 | 0.6755 | 0.50285 | 0.46329 | 0.55215 | 0.52711 | 0.49517 | 0.12062 | 0.38109 | -0.65503 | 0.14438 | -0.061701 | -0.33258 | -0.43107 | -0.41174 | -0.33113 | -0.21356 | -0.18692 | -0.27455 | -0.55487 | -0.81937 | -0.98046 | -0.95168 | -0.62574 | 0.0090511 | 0.7441 | 1.1952 | 1.3697 | 1.3307 | 1.1361 | 0.19862 | 1.0694 | 1.1015 | 1.1163 | 1.143 | 1.3171 | 1.5148 | 1.5511 | 1.4591 | 1.2792 | 1.0559 | 0.7487 | -0.021384 | -2.0509 | 0.39779 | 0.48272 | 0.43261 | 0.58119 | 0.93843 | 1.5144 | 1.5304 | 1.4784 | 1.2313 | 0.82402 | 0.26546 | -0.4555 | -1.125 | -1.4672 | -1.6048 | -1.5333 | -1.4446 | -1.1652 | -0.98143 | -0.9065 | -0.75704 | -0.46915 | -0.88131 | 0.55408 | 0.93547 | 1.1504 | 1.2133 | 0.99133 | 0.70727 | 0.33567 | -0.070876 | -0.48145 | -0.73139 | -0.67363 | -0.48673 | -0.38796 | -0.38834 | -0.58815 | -0.92526 | -1.3331 | -1.5459 | -1.5199 | -1.2101 | -0.69777 | -0.086322 | 0.3417 | 0.79995 | 1.1172 | 1.3235 | 1.4966 | 1.4313 | 1.3055 | 1.1939 | 1.2141 | 1.333 | 1.2627 | 1.2644 | 1.3258 | 1.5907 | 2.0493 | 2.4259 | 2.4312 | 2.2584 | 1.8665 | 1.2914 | 0.47254 | -0.458 | -1.1955 | -1.6123 | -1.6499 | -1.4287 | -1.1222 | -0.83784 | -0.63025 | -0.57698 | -0.59868 | -0.6157 | -0.67293 | -0.52022 | -0.12189 | 0.35101 | 0.67834 | 0.87083 | 0.96668 | 0.89505 | 0.73498 | 0.51481 | 0.33508 | 0.22812 | 0.15489 | 0.24372 | 0.33783 | 0.2443 | -0.057267 | -0.29243 | -0.27678 | -0.28687 | -0.43207 | -0.3941 | -0.51892 | -0.59015 | -0.69728 | -0.84163 | -1.0319 | -0.95744 | -0.73214 | -0.49806 | -0.15932 | 0.29232 | 0.76552 | 1.132 | 1.4594 | 1.73 | 2.0536 | 2.3679 | 2.3398 | 2.4687 | 2.4902 | 2.3677 | 2.0591 | 1.724 | 1.5728 | 1.6337 | 1.8347 | 1.9327 | 1.9746 | 1.9122
|  | 540 | 1.0186 | 0.61556 | 0.46772 | 0.72117 | 0.95873 | 1.1925 | 1.4118 | 1.3742 | 1.0705 | 0.56262 | 0.23774 | 0.20753 | 0.30045 | 0.42971 | 0.30414 | -0.018167 | -0.3953 | -0.89718 | -1.378 | -1.8457 | -2.1987 | -2.4532 | -2.4117 | -2.2369 | -1.9333 | -1.7299 | -1.5641 | -1.4432 | -1.3649 | -1.0376 | -0.65869 | -0.10662 | 0.39393 | 0.82143 | 0.4426 | 1.2658 | 1.4622 | 1.5811 | 1.7287 | 1.9452 | 2.3886 | 2.6259 | 2.7389 | 2.6237 | 2.3658 | 2.0642 | 1.8445 | 1.8493 | 2.02 | 2.1947 | 2.1972 | 2.1023 | 1.9387 | 1.7038 | 1.519 | 1.5139 | 1.5965 | 1.7039 | 1.8253 | 1.8972 | 1.8376 | 1.6029 | 1.2763 | 0.78759 | 0.54998 | 0.41324 | 0.39772 | 0.54412 | 0.57304 | 0.52895 | 0.38682 | 0.21588 | -0.25517 | 0.095906 | 0.061527 | -0.1028 | -0.16422 | 0.029306 | 0.083356 | 0.027901 | -0.04745 | -0.18939 | -0.48269 | -0.75892 | -1.0055 | -1.1893 | -0.99562 | -0.34379 | 0.52231 | 1.1588 | 1.5085 | 1.5836 | 1.3179 | 0.26683 | 1.2772 | 1.6962 | 1.8572 | 1.8451 | 1.8082 | 1.7561 | 1.6444 | 1.5513 | 1.4024 | 1.2641 | 0.51617 | -1.8279 | 0.519 | 0.27218 | -0.1108 | -0.26108 | 0.16844 | 1.066 | 1.9941 | 2.0983 | 1.996 | 1.6264 | 1.1088 | 0.32722 | -0.55452 | -1.3104 | -1.6084 | -1.6429 | -1.4632 | -1.3234 | -1.1738 | -1.1907 | -1.3124 | -1.2011 | -0.72515 | -0.80128 | 0.95279 | 1.762 | 2.078 | 2.1387 | 1.7432 | 1.2352 | 0.65948 | 0.024926 | -0.56166 | -0.84739 | -0.61037 | -0.24814 | -0.067143 | -0.11563 | -0.42977 | -0.92017 | -1.457 | -1.7482 | -1.778 | -1.2619 | -0.57982 | 0.038056 | 0.33103 | 0.80886 | 1.0962 | 1.4932 | 1.8214 | 1.8381 | 1.6831 | 1.5024 | 1.4048 | 1.3286 | 1.0612 | 0.93518 | 1.136 | 1.6738 | 2.3529 | 2.9455 | 3.0989 | 2.8822 | 2.369 | 1.6461 | 0.68786 | -0.44857 | -1.2802 | -1.7211 | -1.6482 | -1.3115 | -1.0199 | -0.85005 | -0.81714 | -0.90982 | -0.93431 | -0.88907 | -0.93433 | -0.51297 | 0.1615 | 0.79835 | 1.1957 | 1.3503 | 1.2833 | 1.0803 | 0.85493 | 0.57542 | 0.38749 | 0.37987 | 0.41746 | 0.46876 | 0.42359 | 0.072974 | -0.42369 | -0.73231 | -0.62888 | -0.2195 | 0.094964 | 0.30586 | 0.22567 | -0.02519 | -0.33405 | -0.67758 | -1.1097 | -0.98995 | -0.59496 | -0.2155 | 0.10533 | 0.4357 | 0.68942 | 0.94871 | 1.2848 | 1.7931 | 2.3422 | 2.8284 | 3.1742 | 3.3987 | 3.3898 | 3.0841 | 2.6119 | 2.0525 | 1.7285 | 1.6686 | 1.7991 | 1.8942 | 1.932 | 1.9069
|  | 564 | 0.99457 | 0.53786 | 0.39622 | 0.56984 | 1.0119 | 1.4079 | 1.7471 | 1.7292 | 1.2964 | 0.584 | 0.38217 | 0.51255 | 0.96431 | 1.2726 | 1.0655 | 0.50846 | -0.15449 | -0.82544 | -1.4743 | -2.0975 | -2.6458 | -2.8828 | -2.5603 | -2.1179 | -1.6234 | -1.3397 | -1.1104 | -1.0549 | -0.89036 | -0.51414 | -0.14501 | 0.39886 | 0.90768 | 1.1578 | 0.57199 | 1.3471 | 1.5049 | 1.612 | 1.8677 | 2.2104 | 2.8091 | 3.3273 | 3.5391 | 3.3903 | 2.9998 | 2.4642 | 2.1794 | 2.2628 | 2.502 | 2.7215 | 2.6597 | 2.3525 | 2.0208 | 1.6868 | 1.3768 | 1.3514 | 1.5251 | 1.8036 | 2.058 | 2.2004 | 2.2492 | 1.8219 | 1.3816 | 0.86347 | 0.49086 | 0.4602 | 0.47983 | 0.60571 | 0.67211 | 0.59583 | 0.4393 | 0.34536 | -0.1036 | 0.19791 | 0.34308 | 0.32954 | 0.31754 | 0.47959 | 0.50185 | 0.27451 | 0.11935 | -0.10469 | -0.42953 | -0.63521 | -0.95325 | -1.2287 | -1.0332 | -0.31768 | 0.4768 | 1.1892 | 1.7143 | 1.8585 | 1.6055 | 0.2322 | 1.6289 | 2.0862 | 2.4274 | 2.5694 | 2.3033 | 2.0896 | 1.9893 | 2.063 | 1.8347 | 0.96039 | -1.0837 | 1.0431 | 0.75704 | 0.24157 | -0.35795 | -0.54557 | 0.049045 | 1.1754 | 2.1396 | 2.302 | 2.155 | 1.7171 | 1.1258 | 0.29252 | -0.65706 | -1.3697 | -1.666 | -1.6283 | -1.4212 | -1.195 | -1.1698 | -1.2473 | -1.4015 | -1.3359 | -0.77674 | -0.59812 | 1.3532 | 2.2442 | 2.6346 | 2.7416 | 2.2533 | 1.6324 | 1.0119 | 0.34486 | -0.36454 | -0.70904 | -0.3723 | 0.088654 | 0.30956 | 0.16338 | -0.18683 | -0.74332 | -1.3457 | -1.6782 | -1.672 | -1.1792 | -0.39044 | 0.21448 | 0.52121 | 1.0428 | 1.4495 | 1.931 | 2.2568 | 2.3214 | 2.1394 | 1.8705 | 1.6076 | 1.3663 | 1.0495 | 0.87838 | 1.2419 | 2.0317 | 2.7531 | 3.4316 | 3.6712 | 3.4373 | 2.8541 | 2.0827 | 1.0715 | -0.082892 | -1.1524 | -1.6831 | -1.5042 | -1.0727 | -0.76591 | -0.75545 | -0.9439 | -1.1999 | -1.3457 | -1.383 | -1.2856 | -0.52303 | 0.55079 | 1.3793 | 1.8046 | 1.9836 | 1.8467 | 1.6078 | 1.4084 | 1.0252 | 0.79549 | 0.84918 | 0.90286 | 0.83764 | 0.62756 | 0.1267 | -0.52557 | -0.92735 | -0.73211 | -0.088839 | 0.65863 | 1.0306 | 0.99134 | 0.62401 | 0.094964 | -0.40535 | -0.82601 | -0.81666 | -0.4226 | 0.19243 | 0.54673 | 0.68309 | 0.77348 | 0.96971 | 1.3218 | 1.95 | 2.6671 | 3.3694 | 4.1582 | 4.5419 | 4.3812 | 3.8785 | 3.2364 | 2.4957 | 2.0033 | 1.803 | 1.8531 | 1.9382 | 1.9708 | 1.9487
|  | 588 | 1.0975 | 0.66135 | 0.47405 | 0.65037 | 0.91464 | 1.1785 | 1.3034 | 1.3713 | 1.413 | 0.98729 | 0.6848 | 0.43421 | 0.62813 | 0.8121 | 0.6701 | 0.3629 | -0.076751 | -0.64926 | -1.276 | -1.8855 | -2.3956 | -2.6735 | -2.6481 | -2.4137 | -2.0258 | -1.7134 | -1.3525 | -1.0539 | -0.55796 | -0.15877 | 0.028395 | 0.34834 | 0.76471 | 1.161 | 0.5432 | 1.4904 | 1.6302 | 1.7754 | 2.1073 | 2.3595 | 2.6593 | 2.9883 | 3.1583 | 3.1029 | 2.9349 | 2.764 | 2.6237 | 2.4743 | 2.3396 | 2.3446 | 2.2306 | 2.0795 | 1.8597 | 1.6101 | 1.3465 | 1.2382 | 1.3137 | 1.5739 | 1.7904 | 1.6693 | 1.5311 | 1.311 | 1.1597 | 0.83086 | 0.50305 | 0.53599 | 0.56248 | 0.63934 | 0.72048 | 0.6495 | 0.55475 | 0.63325 | 0.24983 | 0.21725 | 0.079323 | 0.054162 | 0.17593 | 0.060047 | -0.095947 | -0.14323 | -0.11143 | -0.29833 | -0.61717 | -0.74454 | -1.0732 | -1.3089 | -1.0649 | -0.38366 | 0.10348 | 0.42736 | 0.75096 | 0.95912 | 1.0727 | 0.35293 | 1.3751 | 1.5925 | 1.8618 | 1.9714 | 1.8965 | 2.0186 | 2.2977 | 2.464 | 1.4656 | -1.2018 | 0.82475 | 0.67676 | 0.49676 | 0.17175 | -0.29896 | -0.50374 | -0.30535 | 0.25034 | 0.80224 | 1.0185 | 0.89411 | 0.61246 | 0.19896 | -0.30452 | -0.82497 | -1.4268 | -1.7345 | -1.7262 | -1.7067 | -1.6046 | -1.4969 | -1.4187 | -1.4517 | -1.3607 | -1.0174 | -1.2106 | 0.43152 | 1.0935 | 1.4369 | 1.527 | 1.2913 | 0.875 | 0.7154 | 0.25495 | -0.32471 | -0.62793 | -0.47278 | -0.27024 | -0.17483 | -0.24732 | -0.45284 | -0.91605 | -1.4264 | -1.7139 | -1.787 | -1.5718 | -1.131 | -0.56754 | -0.17523 | 0.55949 | 1.2047 | 1.507 | 1.5717 | 1.6021 | 1.5851 | 1.5389 | 1.5424 | 1.4208 | 1.1756 | 1.0339 | 1.3836 | 2.0249 | 2.4187 | 2.7189 | 2.8594 | 2.7181 | 2.3783 | 1.9626 | 1.199 | 0.23035 | -0.96148 | -1.5349 | -1.5986 | -1.492 | -1.3313 | -1.223 | -1.1265 | -1.3142 | -1.4936 | -1.51 | -1.2502 | -0.81484 | -0.16642 | 0.49908 | 0.94064 | 1.2232 | 1.3547 | 1.2356 | 0.99903 | 0.65606 | 0.4891 | 0.55998 | 0.67091 | 0.74513 | 0.5995 | 0.15379 | -0.44546 | -0.84232 | -0.79969 | -0.58454 | -0.224 | 0.043809 | 0.092924 | -0.11371 | -0.26196 | -0.38045 | -0.64752 | -0.58785 | -0.26568 | 0.20194 | 0.51945 | 0.83919 | 1.0102 | 1.1521 | 1.5395 | 2.181 | 2.8838 | 3.2668 | 3.7238 | 4.011 | 3.9787 | 3.6474 | 3.2427 | 2.615 | 2.0521 | 1.9399 | 1.9491 | 1.9385 | 1.9834 | 1.9252
|  | 612 | 1.0965 | 0.78014 | 0.60535 | 0.6602 | 0.78822 | 0.96056 | 1.0302 | 1.114 | 1.2201 | 1.0103 | 0.74866 | 0.48412 | 0.61462 | 0.69975 | 0.57055 | 0.34174 | -0.047233 | -0.5245 | -1.0535 | -1.5948 | -2.0847 | -2.4589 | -2.6057 | -2.5623 | -2.269 | -1.8855 | -1.4017 | -1.0192 | -0.54214 | -0.090366 | 0.17389 | 0.51337 | 0.91015 | 1.2525 | 0.50763 | 1.5732 | 1.7491 | 1.8835 | 2.1718 | 2.4173 | 2.7037 | 2.9813 | 3.1437 | 3.1833 | 3.0837 | 2.9271 | 2.8004 | 2.6755 | 2.4962 | 2.387 | 2.1931 | 1.9888 | 1.7597 | 1.5635 | 1.3723 | 1.2291 | 1.1737 | 1.2532 | 1.3654 | 1.3016 | 1.1841 | 1.0258 | 0.90141 | 0.69773 | 0.58995 | 0.62152 | 0.66583 | 0.75755 | 0.82801 | 0.81776 | 0.77263 | 0.7681 | 0.31566 | 0.42809 | 0.33375 | 0.13429 | 0.10037 | -0.049008 | -0.26099 | -0.37501 | -0.40125 | -0.58792 | -0.84681 | -0.92329 | -1.1586 | -1.29 | -1.074 | -0.59596 | -0.22605 | 0.022036 | 0.323 | 0.5907 | 0.86064 | 0.044744 | 1.1905 | 1.4212 | 1.6496 | 1.8094 | 1.8277 | 1.9448 | 2.0818 | 1.5903 | -0.83914 | 0.99648 | 0.83796 | 0.59352 | 0.42452 | 0.20004 | -0.11382 | -0.30532 | -0.31124 | -0.098196 | 0.10068 | 0.13967 | 0.014928 | -0.1726 | -0.39452 | -0.76847 | -1.0053 | -1.402 | -1.6954 | -1.7175 | -1.8286 | -1.8574 | -1.7419 | -1.555 | -1.4159 | -1.2752 | -1.0013 | -1.3344 | -0.10631 | 0.35934 | 0.63133 | 0.76408 | 0.63999 | 0.38979 | 0.49918 | 0.19451 | -0.19575 | -0.39293 | -0.34188 | -0.31698 | -0.3583 | -0.45274 | -0.62226 | -0.94138 | -1.3121 | -1.5444 | -1.687 | -1.6668 | -1.4711 | -1.0066 | -0.60906 | -0.1186 | 0.42747 | 0.83416 | 1.1161 | 1.2884 | 1.4449 | 1.5669 | 1.6667 | 1.605 | 1.4886 | 1.4312 | 1.6381 | 1.9816 | 2.1955 | 2.3469 | 2.3544 | 2.1913 | 1.8793 | 1.4691 | 0.85593 | 0.15017 | -0.76475 | -1.3112 | -1.5227 | -1.6137 | -1.561 | -1.4646 | -1.3719 | -1.4412 | -1.4881 | -1.4424 | -1.217 | -0.86217 | -0.4476 | 0.0053884 | 0.33554 | 0.54138 | 0.66151 | 0.67783 | 0.65994 | 0.59581 | 0.56872 | 0.69168 | 0.78717 | 0.82041 | 0.63772 | 0.28759 | -0.15542 | -0.55709 | -0.73607 | -0.83076 | -0.7959 | -0.67789 | -0.56677 | -0.61896 | -0.63556 | -0.49938 | -0.5213 | -0.35801 | -0.050927 | 0.37942 | 0.66994 | 0.95796 | 1.1873 | 1.4008 | 1.8079 | 2.3326 | 2.9139 | 3.25 | 3.5948 | 3.768 | 3.7213 | 3.4341 | 2.9829 | 2.5216 | 2.1538 | 2.1434 | 2.089 | 1.9477 | 1.9209 | 1.8249
|  | 636 | 1.2011 | 0.98544 | 0.82521 | 0.77414 | 0.79529 | 0.86866 | 0.90787 | 0.95156 | 1.0196 | 0.92372 | 0.8398 | 0.65901 | 0.75331 | 0.7683 | 0.65657 | 0.46036 | 0.12534 | -0.27793 | -0.70517 | -1.1728 | -1.6448 | -2.0625 | -2.3659 | -2.5456 | -2.3667 | -1.8572 | -1.2829 | -0.90834 | -0.39177 | 0.11973 | 0.47041 | 0.82832 | 1.2191 | 1.4907 | 0.54657 | 1.7444 | 1.9367 | 2.0686 | 2.3211 | 2.5874 | 2.8653 | 3.1406 | 3.345 | 3.4415 | 3.3878 | 3.2378 | 3.1223 | 3.0016 | 2.7897 | 2.5932 | 2.3202 | 2.0203 | 1.8221 | 1.6428 | 1.4872 | 1.3223 | 1.1767 | 1.1213 | 1.1306 | 1.0844 | 1.0494 | 0.95397 | 0.85691 | 0.7159 | 0.71975 | 0.81264 | 0.88233 | 1.0238 | 1.1134 | 1.1477 | 1.1219 | 1.0707 | 0.58119 | 0.75506 | 0.71525 | 0.37063 | 0.23113 | -0.017897 | -0.31623 | -0.49177 | -0.60197 | -0.79423 | -1.0214 | -1.0319 | -1.127 | -1.1616 | -1.0027 | -0.70822 | -0.44997 | -0.24472 | 0.031613 | 0.32496 | 0.6654 | -0.078786 | 1.1129 | 1.3764 | 1.6382 | 1.876 | 1.9279 | 1.9384 | 1.4079 | -0.95983 | 1.1201 | 1.1697 | 0.87493 | 0.61192 | 0.47351 | 0.36144 | 0.10609 | -0.054897 | -0.16471 | -0.18574 | -0.23832 | -0.40235 | -0.57796 | -0.69798 | -0.69776 | -1.031 | -1.0201 | -1.232 | -1.5008 | -1.4874 | -1.745 | -1.8445 | -1.6868 | -1.4173 | -1.2192 | -1.0719 | -0.91282 | -1.4297 | -0.40743 | -0.12602 | 0.086221 | 0.29825 | 0.28483 | 0.17293 | 0.40071 | 0.26427 | 0.078518 | -0.0057808 | -0.019299 | -0.079606 | -0.23802 | -0.38621 | -0.53302 | -0.77097 | -1.0422 | -1.2422 | -1.4435 | -1.5991 | -1.6409 | -1.2581 | -0.85891 | -0.48589 | 0.0086454 | 0.49224 | 0.89505 | 1.197 | 1.5242 | 1.7907 | 1.943 | 1.9509 | 1.9274 | 1.934 | 2.0292 | 2.1521 | 2.1669 | 2.1804 | 2.0988 | 1.8645 | 1.5388 | 1.1506 | 0.63756 | 0.17878 | -0.43514 | -0.92706 | -1.305 | -1.5918 | -1.6306 | -1.5313 | -1.4398 | -1.417 | -1.3556 | -1.2514 | -1.0575 | -0.79638 | -0.53619 | -0.24789 | -0.045635 | 0.077547 | 0.16904 | 0.29757 | 0.49356 | 0.66385 | 0.7776 | 0.93589 | 1.0791 | 1.0485 | 0.85923 | 0.56509 | 0.20406 | -0.1978 | -0.53353 | -0.85226 | -1.1017 | -1.1598 | -0.97893 | -0.87461 | -0.80269 | -0.56098 | -0.37714 | -0.016877 | 0.31807 | 0.75665 | 0.98305 | 1.2187 | 1.5242 | 1.7953 | 2.2003 | 2.6018 | 3.088 | 3.3895 | 3.7195 | 3.845 | 3.7354 | 3.5134 | 3.0973 | 2.7614 | 2.5479 | 2.4858 | 2.354 | 2.1036 | 1.9684 | 1.872
|  | 660 | 1.5775 | 1.4096 | 1.2575 | 1.1365 | 1.049 | 1.0216 | 1.0188 | 1.07 | 1.093 | 1.0828 | 1.143 | 1.0838 | 1.0773 | 1.0466 | 0.9741 | 0.83544 | 0.56189 | 0.2541 | -0.1824 | -0.61653 | -1.0217 | -1.4933 | -1.9607 | -2.3774 | -2.298 | -1.7053 | -1.0832 | -0.55182 | 0.027885 | 0.51616 | 0.9522 | 1.3275 | 1.7231 | 2.0418 | 0.86567 | 2.1585 | 2.3544 | 2.4567 | 2.6859 | 2.9491 | 3.2514 | 3.5662 | 3.8928 | 4.034 | 4.0403 | 3.983 | 3.8681 | 3.7235 | 3.4806 | 3.16 | 2.7157 | 2.3256 | 2.1205 | 2.0697 | 1.8912 | 1.6814 | 1.415 | 1.2538 | 1.1961 | 1.1418 | 1.1811 | 1.16 | 1.1442 | 1.0877 | 1.1619 | 1.2695 | 1.2934 | 1.4378 | 1.6273 | 1.7706 | 1.7441 | 1.6675 | 1.1411 | 1.3291 | 1.1861 | 0.78948 | 0.48503 | 0.18207 | -0.1477 | -0.34686 | -0.47218 | -0.64035 | -0.83342 | -0.80775 | -0.84171 | -0.76791 | -0.7118 | -0.47573 | -0.34348 | -0.12945 | 0.054188 | 0.34535 | 0.71015 | 0.014486 | 1.336 | 1.6527 | 1.9747 | 2.2447 | 2.3407 | 1.8196 | -0.63766 | 1.6654 | 1.6805 | 1.3871 | 1.0788 | 0.80622 | 0.68177 | 0.70641 | 0.61302 | 0.40019 | 0.15066 | -0.15974 | -0.44014 | -0.74796 | -0.98039 | -1.0764 | -1.0153 | -1.0221 | -1.0188 | -0.95163 | -1.0135 | -1.1446 | -1.3944 | -1.5601 | -1.2409 | -0.70536 | -0.51708 | -0.41834 | -0.43976 | -1.1063 | -0.26991 | -0.22402 | -0.029491 | 0.18445 | 0.29249 | 0.3729 | 0.53565 | 0.7354 | 0.67625 | 0.54955 | 0.53791 | 0.32585 | -0.016388 | -0.039483 | -0.1353 | -0.35793 | -0.62344 | -0.79652 | -1.0684 | -1.4053 | -1.6215 | -1.4169 | -1.1004 | -0.67313 | -0.25863 | 0.20078 | 0.74853 | 1.2543 | 1.8016 | 2.1599 | 2.3078 | 2.4722 | 2.5735 | 2.6417 | 2.6462 | 2.6557 | 2.5258 | 2.3856 | 2.2334 | 1.8305 | 1.4591 | 1.1141 | 0.58179 | 0.37351 | 0.094502 | -0.35004 | -0.86194 | -1.299 | -1.471 | -1.3966 | -1.3086 | -1.2293 | -1.1216 | -0.98313 | -0.82804 | -0.64301 | -0.46827 | -0.31843 | -0.18851 | -0.059632 | 0.036775 | 0.28437 | 0.70465 | 0.94008 | 1.1445 | 1.3812 | 1.5477 | 1.4702 | 1.3934 | 1.1473 | 0.74593 | 0.31218 | -0.18106 | -0.70103 | -1.1819 | -1.435 | -1.2027 | -0.89956 | -0.54934 | -0.25964 | 0.25983 | 0.62034 | 0.9727 | 1.378 | 1.5582 | 1.7485 | 2.078 | 2.3792 | 2.773 | 3.1338 | 3.5111 | 3.8211 | 4.1083 | 4.2845 | 4.1685 | 4.057 | 3.8297 | 3.5034 | 3.4217 | 3.1685 | 2.884 | 2.5469 | 2.27 | 2.1547
|  | 684 | 1.6628 | 1.5237 | 1.4512 | 1.2983 | 1.3435 | 1.1923 | 1.0096 | 1.2594 | 1.2619 | 1.265 | 1.3376 | 1.2924 | 1.3083 | 1.2341 | 1.1778 | 1.1305 | 0.93032 | 0.55238 | 0.10646 | -0.15909 | -0.54328 | -1.2233 | -1.7812 | -2.1017 | -2.0478 | -1.6633 | -1.12 | -0.57193 | 0.09703 | 0.5205 | 0.9993 | 1.4599 | 1.7912 | 2.2996 | 1.5333 | 2.759 | 2.7149 | 2.9207 | 3.2466 | 3.4951 | 3.7475 | 4.0162 | 4.3095 | 4.5302 | 4.5223 | 4.3405 | 4.2435 | 4.1297 | 3.793 | 3.3603 | 2.8224 | 2.4102 | 2.169 | 2.246 | 2.1178 | 1.7865 | 1.4915 | 1.3776 | 1.3063 | 1.1725 | 1.1238 | 1.2119 | 1.2205 | 1.14 | 1.185 | 1.3239 | 1.3599 | 1.4838 | 1.7269 | 1.9115 | 1.8669 | 1.7545 | 1.3379 | 1.575 | 1.2981 | 0.8962 | 0.6 | 0.27247 | -0.10966 | -0.44101 | -0.7237 | -0.95912 | -1.2442 | -1.2523 | -1.1485 | -1.0474 | -0.96212 | -0.66553 | -0.45446 | -0.38345 | -0.074851 | 0.37942 | 0.72627 | 0.036874 | 1.397 | 1.751 | 2.1665 | 2.3555 | 1.7946 | -0.39143 | 1.84 | 1.8116 | 1.6393 | 1.387 | 1.0725 | 0.78761 | 0.4384 | 0.52503 | 0.72897 | 0.34351 | -0.046377 | -0.18047 | -0.61585 | -1.0579 | -1.361 | -1.4764 | -1.5119 | -1.4993 | -1.3615 | -1.2323 | -1.1718 | -1.1499 | -1.3502 | -1.6081 | -1.3184 | -0.90413 | -0.61842 | -0.51843 | -0.59577 | -1.3643 | -0.45066 | -0.45764 | -0.39097 | -0.2691 | -0.24262 | -0.17222 | 0.097717 | 0.35202 | 0.39354 | 0.38096 | 0.45153 | 0.30653 | -0.030577 | 0.50716 | 0.75939 | 0.091704 | -0.64595 | -0.90356 | -1.1673 | -1.4915 | -1.7924 | -1.6233 | -1.3761 | -1.0775 | -0.74507 | -0.19264 | 0.4849 | 1.07 | 1.6496 | 2.2272 | 2.6273 | 2.6805 | 2.8144 | 2.8015 | 2.7002 | 2.6392 | 2.5364 | 2.2932 | 2.0327 | 1.645 | 1.2481 | 0.84834 | 0.3664 | 0.149 | 0.012862 | -0.31817 | -0.77939 | -1.1535 | -1.2802 | -1.2125 | -1.1299 | -1.132 | -1.1232 | -1.0052 | -0.81508 | -0.69179 | -0.55037 | -0.41093 | -0.28708 | -0.23588 | -0.25772 | 0.3262 | 1.1039 | 1.1401 | 1.1177 | 1.4279 | 1.5617 | 1.6604 | 1.7899 | 1.6213 | 1.2173 | 0.78426 | 0.24128 | -0.50623 | -1.1332 | -1.3127 | -1.1351 | -0.82469 | -0.4306 | -0.050518 | 0.63767 | 1.0701 | 1.3758 | 1.8437 | 2.2406 | 2.3219 | 2.6555 | 3.0264 | 3.314 | 3.6411 | 3.9848 | 4.24 | 4.4529 | 4.594 | 4.6009 | 4.5266 | 4.2997 | 4.0096 | 3.8791 | 3.5815 | 3.1516 | 2.7179 | 2.3316 | 2.2018
|  | 708 | 1.3548 | 1.1968 | 1.1942 | 1.1759 | 1.202 | 1.1223 | 1.0122 | 1.0676 | 1.0027 | 0.94614 | 0.93332 | 0.90741 | 0.89405 | 0.82702 | 0.7612 | 0.76219 | 0.55373 | 0.2323 | -0.061266 | -0.31602 | -0.70716 | -1.2209 | -1.6364 | -1.8624 | -1.862 | -1.6928 | -1.3429 | -0.96121 | -0.5023 | -0.052764 | 0.41909 | 0.91439 | 1.2856 | 1.9816 | 1.2476 | 2.7731 | 2.8993 | 3.2197 | 3.5536 | 3.7757 | 3.9182 | 4.0426 | 4.2026 | 4.3212 | 4.2545 | 4.0653 | 3.9137 | 3.7155 | 3.4018 | 2.9706 | 2.4938 | 2.0895 | 1.9919 | 2.0335 | 1.8824 | 1.6229 | 1.3612 | 1.2817 | 1.1608 | 0.97447 | 0.89177 | 0.90228 | 0.9112 | 0.86917 | 0.92577 | 1.0325 | 1.1245 | 1.3373 | 1.5881 | 1.7315 | 1.7708 | 1.6772 | 1.1064 | 1.3465 | 1.2558 | 0.872 | 0.57256 | 0.23227 | -0.16389 | -0.5926 | -1.03 | -1.4238 | -1.7536 | -1.9177 | -1.8611 | -1.707 | -1.5215 | -1.2117 | -0.74817 | -0.5954 | -0.2771 | 0.17585 | 0.52146 | -0.29891 | 1.1214 | 1.526 | 1.9061 | 1.7166 | -0.47488 | 1.9206 | 1.9023 | 1.7074 | 1.522 | 1.2743 | 0.96708 | 0.57497 | 0.21304 | 0.16747 | 0.23313 | -0.0067485 | -0.31062 | -0.52031 | -0.87624 | -1.2961 | -1.6327 | -1.8665 | -1.9938 | -1.9837 | -1.8499 | -1.6881 | -1.5398 | -1.3827 | -1.4215 | -1.6268 | -1.4477 | -1.1468 | -0.73964 | -0.5474 | -0.54076 | -1.2462 | -0.4821 | -0.53883 | -0.57201 | -0.56825 | -0.60807 | -0.53048 | -0.34822 | -0.16244 | -0.049282 | 0.10106 | 0.25233 | 0.14333 | -0.024925 | 0.59215 | 0.71281 | 0.055543 | -0.69586 | -1.0277 | -1.3108 | -1.7503 | -2.0121 | -1.9044 | -1.6538 | -1.3872 | -1.0325 | -0.49726 | 0.14268 | 0.73599 | 1.3188 | 1.8528 | 2.3436 | 2.4794 | 2.6479 | 2.6602 | 2.538 | 2.4254 | 2.2858 | 2.0447 | 1.7577 | 1.4298 | 1.0442 | 0.62944 | 0.19872 | -0.1179 | -0.31757 | -0.58988 | -0.95018 | -1.2585 | -1.3939 | -1.2886 | -1.2252 | -1.2684 | -1.2914 | -1.204 | -1.055 | -0.92301 | -0.74316 | -0.56181 | -0.41639 | -0.35182 | -0.34964 | 0.094802 | 0.6383 | 0.62813 | 0.60638 | 0.82033 | 0.95976 | 1.0683 | 1.1269 | 0.96498 | 0.62632 | 0.2681 | -0.14153 | -0.70966 | -1.1559 | -1.3077 | -1.2358 | -1.0313 | -0.72665 | -0.38422 | 0.21418 | 0.74813 | 1.2047 | 1.8129 | 2.3274 | 2.5634 | 2.8761 | 3.2115 | 3.4577 | 3.7119 | 4.0043 | 4.1964 | 4.3332 | 4.4264 | 4.4152 | 4.2642 | 4.0235 | 3.775 | 3.5449 | 3.234 | 2.8222 | 2.37 | 1.9741 | 1.8648
|  | 732 | 1.2729 | 1.1717 | 1.23 | 1.2556 | 1.2765 | 1.1985 | 1.0662 | 1.0386 | 0.94617 | 0.86302 | 0.77464 | 0.76198 | 0.7358 | 0.68131 | 0.52893 | 0.42998 | 0.31502 | 0.23624 | 0.051952 | -0.23959 | -0.59888 | -0.98963 | -1.331 | -1.5612 | -1.6129 | -1.5794 | -1.3632 | -1.1771 | -0.95468 | -0.51882 | -0.010911 | 0.53595 | 0.99485 | 1.8541 | 0.37486 | 3.0022 | 3.5047 | 3.8042 | 4.0804 | 4.2164 | 4.2829 | 4.2708 | 4.3257 | 4.382 | 4.2933 | 4.108 | 3.8666 | 3.6182 | 3.2713 | 2.8455 | 2.3395 | 1.8763 | 1.8161 | 1.9341 | 1.8593 | 1.6767 | 1.4437 | 1.3306 | 1.1702 | 0.92726 | 0.82047 | 0.78284 | 0.81512 | 0.82817 | 0.90884 | 1.0046 | 1.0968 | 1.3439 | 1.5678 | 1.7138 | 0.80049 | 1.7676 | -0.60556 | 1.4214 | 1.4453 | 1.07 | 0.74956 | 0.39335 | -0.053821 | -0.51297 | -1.0116 | -1.5449 | -2.0671 | -2.3802 | -2.3834 | -2.1602 | -1.8773 | -1.5587 | -0.94779 | -0.59281 | -0.20113 | 0.20358 | 0.52896 | -0.98135 | 1.1261 | 1.4453 | 1.5169 | -0.8397 | 1.8661 | 2.1928 | 2.049 | 1.8586 | 1.6213 | 1.3276 | 0.97525 | 0.60321 | 0.24237 | 0.10965 | 0.071254 | -0.1196 | -0.38549 | -0.60207 | -0.94432 | -1.3713 | -1.7775 | -2.1189 | -2.2998 | -2.3295 | -2.1484 | -1.9279 | -1.6894 | -1.3732 | -1.3017 | -1.4559 | -1.4198 | -1.0203 | -0.48265 | -0.2656 | -0.27438 | -1.1149 | -0.35289 | -0.47363 | -0.58833 | -0.66085 | -0.81742 | -0.75189 | -0.57219 | -0.43187 | -0.30006 | 0.023136 | 0.29004 | 0.27429 | 0.18784 | 0.36531 | 0.35445 | -0.071225 | -0.62642 | -0.78454 | -1.0046 | -1.7893 | -2.1115 | -2.0758 | -1.8665 | -1.5399 | -1.1575 | -0.67744 | -0.10394 | 0.50821 | 1.0896 | 1.5816 | 2.1059 | 2.387 | 2.6337 | 2.6921 | 2.5572 | 2.4151 | 2.2178 | 1.9589 | 1.6681 | 1.3426 | 0.98607 | 0.57985 | 0.14395 | -0.24565 | -0.45921 | -0.68101 | -0.96357 | -1.2338 | -1.4593 | -1.3668 | -1.2705 | -1.2742 | -1.3195 | -1.2632 | -1.1734 | -1.0256 | -0.84093 | -0.60953 | -0.40861 | -0.27251 | -0.1986 | -0.00026316 | 0.25246 | 0.27147 | 0.25443 | 0.28599 | 0.27221 | 0.34549 | 0.48234 | 0.49355 | 0.31092 | 0.066791 | -0.20862 | -0.61359 | -0.9497 | -1.1586 | -1.1594 | -1.0343 | -0.77401 | -0.49689 | -0.2325 | 0.75982 | 1.3676 | 2.0903 | 2.6445 | 2.9995 | 3.3458 | 3.6396 | 3.8281 | 3.9852 | 4.2027 | 4.3329 | 4.447 | 4.5351 | 4.5209 | 4.4011 | 4.1805 | 3.9051 | 3.5902 | 3.2115 | 2.7431 | 2.2069 | 1.7331 | 1.553
|  | 756 | 1.1277 | 1.1531 | 1.2831 | 1.3275 | 1.3476 | 1.2775 | 1.1411 | 1.0467 | 0.88467 | 0.7589 | 0.59923 | 0.57821 | 0.58716 | 0.57254 | 0.44196 | 0.29973 | 0.27087 | 0.31 | 0.14367 | -0.11926 | -0.42296 | -0.73751 | -1.044 | -1.2811 | -1.3265 | -1.4133 | -1.309 | -1.2524 | -1.3499 | -0.9998 | -0.41574 | 0.23315 | 0.91684 | 1.9084 | -0.78424 | 3.6918 | 4.1927 | 4.4546 | 4.7051 | 4.7239 | 4.6715 | 4.5304 | 4.4908 | 4.5044 | 4.3728 | 4.2064 | 3.919 | 3.6289 | 3.283 | 2.7886 | 2.3286 | 1.9505 | 1.7742 | 1.9069 | 1.9247 | 1.8356 | 1.6479 | 1.48 | 1.1982 | 0.93851 | 0.82082 | 0.74554 | 0.75832 | 0.7656 | 0.92103 | 1.0661 | 1.1769 | 1.3986 | 1.6201 | 1.8277 | 1.9438 | 1.8359 | 1.5194 | 1.9812 | 1.6948 | 1.3762 | 1.0318 | 0.68024 | 0.19467 | -0.29822 | -0.72411 | -1.5098 | -2.2857 | -2.759 | -2.8395 | -2.5315 | -2.0724 | -1.6683 | -0.98114 | -0.40505 | 0.022368 | 0.42433 | 1.0486 | -1.7033 | 0.64891 | 0.94521 | -1.0046 | 1.294 | 2.4721 | 2.3497 | 2.2965 | 2.1806 | 1.8636 | 1.6667 | 1.4189 | 0.9529 | 0.78909 | 0.57273 | 0.27276 | 0.15425 | -0.0089806 | -0.4047 | -0.70782 | -1.1809 | -1.7558 | -2.1631 | -2.3889 | -2.5726 | -2.2611 | -1.9042 | -1.5566 | -0.83942 | -0.77541 | -0.66464 | -0.48967 | -0.11653 | 0.25125 | 0.67807 | 0.36499 | -0.7844 | 0.18132 | -0.14453 | -0.4104 | -0.34426 | -0.82667 | -0.89014 | -0.48802 | -0.51451 | -0.32451 | 0.41831 | 0.66181 | 0.83726 | 1.0627 | 0.79029 | 0.63435 | 0.23605 | -0.40751 | -0.35056 | -0.77302 | -1.7283 | -1.9939 | -2.0917 | -1.9655 | -1.4357 | -1.0978 | -0.80283 | -0.17427 | 0.50687 | 1.0459 | 1.7029 | 2.4366 | 2.719 | 3.052 | 3.0341 | 2.7296 | 2.4509 | 2.1612 | 1.8842 | 1.6556 | 1.3935 | 1.0312 | 0.72668 | 0.1858 | -0.3225 | -0.38824 | -0.61968 | -0.88797 | -0.95925 | -1.1009 | -1.142 | -1.0649 | -1.1664 | -1.2355 | -1.1532 | -1.1745 | -1.0736 | -0.8131 | -0.54594 | -0.28379 | -0.036256 | 0.039579 | 0.13171 | 0.2511 | 0.13844 | -0.035491 | -0.14365 | -0.29121 | -0.22244 | 0.045921 | 0.17135 | 0.13708 | 0.039955 | -0.12242 | -0.47446 | -0.78674 | -1.0007 | -1.049 | -1.0454 | -0.86929 | -0.60674 | -1.8553 | 0.28078 | 1.5422 | 2.4114 | 3.0559 | 3.5164 | 3.8265 | 4.067 | 4.2079 | 4.301 | 4.439 | 4.4837 | 4.5758 | 4.698 | 4.6694 | 4.5521 | 4.3453 | 4.0455 | 3.7086 | 3.2648 | 2.7099 | 2.116 | 1.5816 | 1.2726
|  | 780 | 1.4048 | 1.5967 | 1.8014 | 1.8913 | 1.8653 | 1.8351 | 1.6742 | 1.5546 | 1.3391 | 1.1704 | 0.96984 | 0.93119 | 0.98828 | 1.0537 | 1.0568 | 1.0241 | 0.95814 | 0.97437 | 0.76331 | 0.52206 | 0.24182 | -0.010387 | -0.35363 | -0.58266 | -0.6263 | -0.80129 | -0.80636 | -0.87301 | -1.2299 | -0.9755 | -0.25745 | 0.50619 | 1.4902 | 2.7319 | -0.4707 | 4.8328 | 5.3615 | 5.6347 | 5.8273 | 5.6814 | 5.4306 | 5.1803 | 5.0495 | 4.9754 | 4.7947 | 4.6731 | 4.4168 | 4.181 | 3.757 | 3.1885 | 2.7255 | 2.4801 | 2.2569 | 2.4005 | 2.4565 | 2.4132 | 2.3189 | 2.0749 | 1.6291 | 1.3489 | 1.1929 | 1.0513 | 1.0629 | 1.0802 | 1.325 | 1.5207 | 1.6863 | 1.9252 | 2.1931 | 2.3973 | 2.7386 | 2.6842 | 2.4328 | 2.8738 | 2.6016 | 2.1783 | 1.7712 | 1.4188 | 0.90487 | 0.27233 | -0.26593 | -1.1354 | -2.0436 | -2.6415 | -2.8012 | -2.4479 | -1.8875 | -1.2921 | -0.52257 | 0.16675 | 0.6145 | 1.1148 | 1.8884 | -3.4426 | -1.4015 | -1.1393 | 0.18314 | 2.9943 | 3.169 | 3.0966 | 3.0788 | 3.0751 | 2.7261 | 2.5161 | 2.2578 | 1.8641 | 1.6684 | 1.4443 | 1.163 | 0.98841 | 0.78371 | 0.30697 | -0.038996 | -0.61521 | -1.2867 | -1.854 | -2.1778 | -2.3134 | -2.0204 | -1.4741 | -0.82164 | -0.17654 | 0.17234 | 0.63697 | 1.0214 | 1.3417 | 1.5108 | 1.7452 | 1.5446 | -0.80113 | 1.0748 | 0.67188 | 0.30038 | 0.12946 | -0.33108 | -0.41502 | -0.14365 | 0.027457 | 0.3667 | 1.0447 | 1.5198 | 1.9065 | 2.1921 | 1.8669 | 1.5506 | 1.0325 | 0.31671 | 0.014538 | -0.57963 | -1.0724 | -1.3339 | -2.6869 | -1.7514 | -0.85161 | -0.64106 | -0.37132 | 0.29112 | 0.97468 | 1.6358 | 2.4433 | 3.301 | 3.6709 | 3.9588 | 3.8984 | 3.5399 | 3.0249 | 2.606 | 2.3143 | 2.1207 | 1.9307 | 1.6341 | 1.3466 | 0.75368 | 0.12444 | 0.062558 | -0.14499 | -0.2798 | -0.24752 | -0.30756 | -0.41551 | -0.42291 | -0.58714 | -0.64177 | -0.59611 | -0.71638 | -0.64266 | -0.34854 | -0.028119 | 0.27047 | 0.58774 | 0.66031 | 0.71013 | 0.71301 | 0.43502 | 0.10535 | -0.064369 | -0.17405 | -0.051339 | 0.33058 | 0.5269 | 0.64194 | 0.65252 | 0.45942 | 0.10499 | -0.19761 | -0.47684 | -0.6107 | -0.67738 | -0.56198 | -0.31978 | -3.0821 | -0.74385 | 2.4444 | 3.2294 | 3.8596 | 4.3178 | 4.5739 | 4.7775 | 4.9384 | 4.9866 | 5.0353 | 5.0234 | 5.0793 | 5.1827 | 5.1611 | 5.0436 | 4.8624 | 4.5719 | 4.2641 | 3.69 | 3.0651 | 2.4238 | 1.8211 | 1.4293